## Net Analysis
Gross Energy Generation (GWh) | 248.2
Gross Capacity Factor | 47.7%
Loss Factors
Availability
Turbine Availability | 96%
Balance of Plant Availability | 99.7%
Grid Availability | 99.5%
Environmental Curtailment
Sector Management | 100%
High Wind Hysteresis | 98.8%
Icing Shutdown | 99%
Extreme Temperature | 100%
Wakes
Total Wakes | 95.3%
Electrical Efficiency
Total Electrical Efficiency | 97.5%
Consumptive Power | 100%
Turbine Efficiency
Turbine Performance | 98%
Turbulence Intensity | 98.2%
Inflow Angle | 100%
Environmental
Blade Soiling | 98.5%
Blade Degradation | 99.5%
Soft Icing | 99.5%
Aggregate Loss Factor | 81.2%
Net Energy Generation (GWh) | 201.5
Net Capacity Factor | 38.7%
Met Tower Uncertainty (% of P50 Wind Speed) | M0571 | M4666
Measurement | 2.8% | 1.9%
Vertical Extrapolation | 1.4% | 1.5%
MOS Correction | 0.3% | 2.4%
Climatic Variability | 1.2% | 1.3%
Combined Uncertainty | 3.4% | 3.6%
Project Uncertainty (% of P50 Energy) | 1-year | 5-year | 10-year | 20-year
Measurement | 2.6% | 2.6% | 2.6% | 2.6%
Vertical Extrapolation | 1.6% | 1.6% | 1.6% | 1.6%
MOS Correction | 0.8% | 0.8% | 0.8% | 0.8%
Climate Variability | 3.8% | 2% | 1.6% | 1.4%
Spatial Modeling | 4.2% | 4.2% | 4.2% | 4.2%
Power Modeling | 4.4% | 4.4% | 4.4% | 4.4%
Total Uncertainty | 7.9% | 7.1% | 7.1% | 7%
P-level (Capacity Factor) | 1-year | 5-year | 10-year | 20-year
Gross-P50 | 47.7% | 47.7% | 47.7% | 47.7%
Net-P50 | 38.7% | 38.7% | 38.7% | 38.7%
Net-P75 | 36.6% | 36.8% | 36.9% | 36.9%
Net-P90 | 34.8% | 35.2% | 35.2% | 35.2%
Net-P95 | 33.7% | 34.1% | 34.2% | 34.2%
Net-P99 | 31.6% | 32.3% | 32.3% | 32.4%
P-level (GWh/year) | 1-year | 5-year | 10-year | 20-year
Gross-P50 | 248.2 | 248.2 | 248.2 | 248.2
Net-P50 | 201.5 | 201.5 | 201.5 | 201.5
Net-P75 | 190.8 | 191.8 | 191.9 | 192
Net-P90 | 181.2 | 183 | 183.3 | 183.4
Net-P95 | 175.5 | 177.8 | 178.1 | 178.3
Net-P99 | 164.7 | 168 | 168.4 | 168.7
Net Analysis
version 1-1
CLIENT: BLACK HILLS CORP.
PROJECT: BUSCH RANCH II
TURBINE: VESTAS V120-2.2MW
HUB HEIGHT: 80M
ALL DATA PRESENTED IN THIS PRELIMINARY REPORT ARE DRAFT AND ARE SUBJECT TO CHANGE DURING THE FINAL QUALITY CONTROL PROCESS.

## Turbine Means MWh
Turbine ID | Latitude | Longitude | Wind Speed | Density | Gross Generation | Wake Loss | Net Generation
|  |  | m/s | kg/m3 | MWh | % | MWh
T01 | 37.7571 | -104.4568 | 7.44 | 0.98665 | 8851 | 95.55% | 7190 | 8457
T02 | 37.7526 | -104.459 | 7.47 | 0.98688 | 8896 | 95.65% | 7229 | 8509
T03 | 37.75 | -104.4567 | 7.52 | 0.98673 | 8979 | 96.31% | 7346 | 8648
T04 | 37.7595 | -104.4509 | 7.52 | 0.98642 | 8988 | 91.27% | 6975 | 8203
T05 | 37.7574 | -104.4469 | 7.5 | 0.98742 | 8976 | 92.87% | 7092 | 8336
T06 | 37.755 | -104.4419 | 7.44 | 0.98909 | 8912 | 94.26% | 7158 | 8400
T07 | 37.7502 | -104.4401 | 7.47 | 0.98954 | 8968 | 96.43% | 7367 | 8647
T08 | 37.795 | -104.4426 | 7.44 | 0.99161 | 8970 | 95.3% | 7296 | 8549
T09 | 37.7993 | -104.4426 | 7.41 | 0.99227 | 8933 | 96.31% | 7346 | 8603
T10 | 37.7723 | -104.4029 | 7.88 | 0.98913 | 9577 | 95.59% | 7785 | 9155
T11 | 37.7712 | -104.3933 | 7.71 | 0.99115 | 9370 | 95.42% | 7626 | 8941
T12 | 37.7688 | -104.3889 | 7.73 | 0.99186 | 9399 | 95.1% | 7624 | 8938
T13 | 37.7658 | -104.3852 | 7.75 | 0.99237 | 9429 | 95.98% | 7718 | 9050
T14 | 37.7609 | -104.3832 | 7.71 | 0.99332 | 9378 | 96.34% | 7711 | 9035
T15 | 37.756 | -104.3812 | 7.79 | 0.99295 | 9487 | 97.36% | 7876 | 9237
T16 | 37.7906 | -104.4426 | 7.44 | 0.99111 | 8954 | 95.21% | 7273 | 8525
T17 | 37.7845 | -104.4426 | 7.5 | 0.98967 | 9012 | 94.56% | 7263 | 8522
T18 | 37.7809 | -104.4409 | 7.69 | 0.98791 | 9260 | 94.66% | 7451 | 8765
T19 | 37.7731 | -104.4324 | 7.73 | 0.98779 | 9310 | 95.05% | 7518 | 8849
T20 | 37.768 | -104.4324 | 7.69 | 0.98776 | 9255 | 94.59% | 7444 | 8755
T21 | 37.8053 | -104.4064 | 7.67 | 0.9923 | 9280 | 96.67% | 7652 | 8971
T22 | 37.8008 | -104.4054 | 7.69 | 0.99188 | 9311 | 95.74% | 7603 | 8914
T23 | 37.7963 | -104.4044 | 7.66 | 0.9917 | 9283 | 95.43% | 7560 | 8859
T24 | 37.7917 | -104.4034 | 7.71 | 0.99101 | 9349 | 95.82% | 7641 | 8958
T25 | 37.7854 | -104.4106 | 7.76 | 0.99016 | 9415 | 95.68% | 7672 | 9008
T26 | 37.7822 | -104.4073 | 7.68 | 0.99049 | 9307 | 94.45% | 7497 | 8790
T27 | 37.7789 | -104.404 | 7.74 | 0.9901 | 9390 | 94.83% | 7589 | 8905
|  | Total | 7.62 | 0.98997 | 248239 | 95.28% | 201502
Turbine Means MWh
version 1-1
CLIENT: BLACK HILLS CORP.
PROJECT: BUSCH RANCH II
TURBINE: VESTAS V120-2.2MW
HUB HEIGHT: 80M
ALL DATA PRESENTED IN THIS PRELIMINARY REPORT ARE DRAFT AND ARE SUBJECT TO CHANGE DURING THE FINAL QUALITY CONTROL PROCESS.

## Turbine Means CF
Turbine ID | Latitude | Longitude | Wind Speed | Density | Gross Generation | Wake Loss | Net Generation
|  |  | m/s | kg/m3 | % | % | %
T01 | 37.7571 | -104.4568 | 7.44 | 0.98665 | 45.9% | 95.55% | 37.3% | 43.85%
T02 | 37.7526 | -104.459 | 7.47 | 0.98688 | 46.1% | 95.65% | 37.5% | 44.12%
T03 | 37.75 | -104.4567 | 7.52 | 0.98673 | 46.6% | 96.31% | 38.1% | 44.84%
T04 | 37.7595 | -104.4509 | 7.52 | 0.98642 | 46.6% | 91.27% | 36.2% | 42.54%
T05 | 37.7574 | -104.4469 | 7.5 | 0.98742 | 46.5% | 92.87% | 36.8% | 43.23%
T06 | 37.755 | -104.4419 | 7.44 | 0.98909 | 46.2% | 94.26% | 37.1% | 43.56%
T07 | 37.7502 | -104.4401 | 7.47 | 0.98954 | 46.5% | 96.43% | 38.2% | 44.84%
T08 | 37.795 | -104.4426 | 7.44 | 0.99161 | 46.5% | 95.3% | 37.8% | 44.33%
T09 | 37.7993 | -104.4426 | 7.41 | 0.99227 | 46.3% | 96.31% | 38.1% | 44.61%
T10 | 37.7723 | -104.4029 | 7.88 | 0.98913 | 49.7% | 95.59% | 40.4% | 47.47%
T11 | 37.7712 | -104.3933 | 7.71 | 0.99115 | 48.6% | 95.42% | 39.5% | 46.36%
T12 | 37.7688 | -104.3889 | 7.73 | 0.99186 | 48.7% | 95.1% | 39.5% | 46.35%
T13 | 37.7658 | -104.3852 | 7.75 | 0.99237 | 48.9% | 95.98% | 40% | 46.93%
T14 | 37.7609 | -104.3832 | 7.71 | 0.99332 | 48.6% | 96.34% | 40% | 46.85%
T15 | 37.756 | -104.3812 | 7.79 | 0.99295 | 49.2% | 97.36% | 40.8% | 47.9%
T16 | 37.7906 | -104.4426 | 7.44 | 0.99111 | 46.4% | 95.21% | 37.7% | 44.2%
T17 | 37.7845 | -104.4426 | 7.5 | 0.98967 | 46.7% | 94.56% | 37.7% | 44.19%
T18 | 37.7809 | -104.4409 | 7.69 | 0.98791 | 48% | 94.66% | 38.6% | 45.45%
T19 | 37.7731 | -104.4324 | 7.73 | 0.98779 | 48.3% | 95.05% | 39% | 45.89%
T20 | 37.768 | -104.4324 | 7.69 | 0.98776 | 48% | 94.59% | 38.6% | 45.4%
T21 | 37.8053 | -104.4064 | 7.67 | 0.9923 | 48.1% | 96.67% | 39.7% | 46.52%
T22 | 37.8008 | -104.4054 | 7.69 | 0.99188 | 48.3% | 95.74% | 39.4% | 46.22%
T23 | 37.7963 | -104.4044 | 7.66 | 0.9917 | 48.1% | 95.43% | 39.2% | 45.93%
T24 | 37.7917 | -104.4034 | 7.71 | 0.99101 | 48.5% | 95.82% | 39.6% | 46.45%
T25 | 37.7854 | -104.4106 | 7.76 | 0.99016 | 48.8% | 95.68% | 39.8% | 46.71%
T26 | 37.7822 | -104.4073 | 7.68 | 0.99049 | 48.3% | 94.45% | 38.9% | 45.58%
T27 | 37.7789 | -104.404 | 7.74 | 0.9901 | 48.7% | 94.83% | 39.4% | 46.17%
|  | Average | 7.62 | 0.98997 | 47.7% | 95.3% | 38.7%
Turbine Means CF
version 1-1
CLIENT: BLACK HILLS CORP.
PROJECT: BUSCH RANCH II
TURBINE: VESTAS V120-2.2MW
HUB HEIGHT: 80M
ALL DATA PRESENTED IN THIS PRELIMINARY REPORT ARE DRAFT AND ARE SUBJECT TO CHANGE DURING THE FINAL QUALITY CONTROL PROCESS.

## Specifications
Project Specifications
Turbine Type(s): | Vestas V120-2.2MW
Hub Height: | 80m
Turbine Capacity: | 2200 kW
Number of Turbines: | 27
Number of External Turbines: | 50
Number of Future Turbines: | 0
Model Specifications
Reanalysis Dataset: | MERRA2
Number of Years: | 37
WRF Resolution (Temporal Dataset): | 4500m
WRF Resolution (Spatial Dataset): | 500m
TVM Resolution: | 90m
Observational Data
Meteorological Tower(s): | M0571 | M4666 | khokade
Top Sensor Height: | 60m | 59m | 80m
Time Series Start: | 2008-11-07 | 2013-04-19 15:40 | 2012-04-01
Time Series End: | 2014-01-14 23:50 | 2014-04-28 00:50 | 2013-04-01 11:30
Post QC Recovery Rate: | 90.29% | 94.58% | 91.83%
Loss Calculations
Turbine Availability: | Based on Vaisala's experience over the lifetime of a turbine.
Balance of Plant Availability: | This is based on 24 hours of outage time per year.
Grid Availability: | Based on grid availability forecast for the region.
Sector Management: | Standard minimum turbine spacing of five rotor diameters parallel to the dominant wind direction is
tested against the layout.
High Wind Hysteresis: | Based on the percentage of time when the wind speed is below the cut-out and above the re-cut-in wind speed
after a high wind cut-out event.
Icing Shutdown | Based on the percentage of time the turbine blade are expected to be affected by ice build-up.
Extreme Temperature: | Based on the percentage of time when ambient temperature is expected to be above the operating temperature.
Wakes: | Wake loss calculated using Vaisala's proprietary time varying wake model.
Collection System Efficiency: | This value covers the efficiency of all components from the turbines to the substation
Substation Transformer Efficiency: | Vaisala assumes that the plant will be metered on the low voltage side of the substation transformer
HV Transmission Line Efficiency: | Vaisala assumes that the plant will be metered on the low voltage side of the substation transformer
Turbine Performance: | Based on Vaisala’s experience with wind farms in the region, turbines do not perform exactly at the manufacturer's
stated power curve.
Turbulence Intensity: | Turbine inefficiency resulting from the statistical averaging of the power curve and periods of high stability.
Inflow Angle: | Based on the slope of the terrain leading up to the wind turbine.
Blade Soiling: | Turbine inefficiency due to a build up of material on the turbine blades.
Soft Icing: | Turbine inefficiency due to ice build up on blades.
Blade Degradation: | Turbine inefficiency due to damage to the turbine blades cause by debris in the air.
Uncertainty Calculations
Measurement: | Measurement uncertainty covers quality of anemometers, availability of data, tower configuration, boom lengths
and whether towers have been visited in a site visit. It also covers the statistical propagation of these errors
through the shear calculation.
Vertical Extrapolation: | Vertical extrapolation is the process of using tower height wind speeds to estimate hub height wind speeds.
This uncertainty is based on the difference between measurement heights and hub height.
MOS Correction: | MOS correlation uncertainty is based on the length of observational record and the fit of the simulated time series
to the observational data.
Climate Variability: | Climate variability is comprised of three components. The probability that the period Vaisala used as the historic
climate represents the true climate. The probability that the climate of the future prediction period will capture
the true climate and the probability that the climate is changing.
Spatial Modeling: | Spatial modeling captures the effects of mesoscale models calibrated to the met tower locations and its ability to
predict turbine locations. It is comprised of two components, a mesoscale and microscale uncertainty that are
a function of the models that Vaisala uses. This complex uncertainty considers the spatial covariance between
every turbine and met tower location.
Power Modeling: | Power modeling uncertainty is based on the conversion from Gross P50 wind speed to Net P50 energy.
Specifications
version 1-1
CLIENT: BLACK HILLS CORP.
PROJECT: BUSCH RANCH II
TURBINE: VESTAS V120-2.2MW
HUB HEIGHT: 80M
ALL DATA PRESENTED IN THIS PRELIMINARY REPORT ARE DRAFT AND ARE SUBJECT TO CHANGE DURING THE FINAL QUALITY CONTROL PROCESS.

## 8760-avg
Date are in local time (UTC -7)
Values represent the average value for each hour of the year based on the 37-year timeseries
This if NOT a "typical" year
MWh | HOUR
DAY | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
1 | 22.9087 | 25.3695 | 28.2837 | 29.4364 | 29.1861 | 28.1626 | 28.0125 | 26.375 | 25.5917 | 23.3917 | 20.2433 | 19.686 | 19.3689 | 17.6682 | 19.1141 | 19.1501 | 18.6972 | 19.6294 | 22.5985 | 24.2541 | 23.2636 | 25.3252 | 27.1453 | 25.6826
2 | 25.2315 | 26.4263 | 27.9108 | 29.304 | 28.4847 | 27.451 | 27.5236 | 26.0018 | 24.9198 | 22.8112 | 19.0847 | 18.4404 | 18.7969 | 21.598 | 23.3199 | 17.9301 | 17.6253 | 23.5585 | 26.1774 | 30.7251 | 30.9119 | 29.9488 | 29.1385 | 26.8754
3 | 27.0916 | 27.1412 | 29.2554 | 29.9162 | 29.6791 | 30.6646 | 30.7401 | 28.764 | 28.8232 | 27.6149 | 24.3659 | 22.3027 | 22.6727 | 21.7982 | 23.4135 | 24.9808 | 25.3236 | 27.0226 | 29.1925 | 27.9198 | 25.6551 | 22.6796 | 21.8253 | 21.8389
4 | 21.9703 | 20.8531 | 20.5275 | 22.0017 | 23.1844 | 23.0787 | 22.0634 | 20.928 | 21.3597 | 22.7006 | 21.0087 | 21.9092 | 22.0641 | 21.0715 | 21.4092 | 22.7268 | 22.2416 | 23.5719 | 26.9648 | 25.8619 | 26.1468 | 26.9146 | 27.9549 | 29.8484
5 | 29.7414 | 29.1969 | 28.3883 | 27.51 | 26.9774 | 25.5997 | 23.6454 | 24.2983 | 25.0381 | 24.4134 | 22.7434 | 18.9183 | 18.0398 | 19.1528 | 20.2981 | 22.8665 | 23.7256 | 25.4957 | 27.2469 | 27.5122 | 25.16 | 28.1976 | 28.7275 | 24.3034
6 | 24.2984 | 23.7789 | 23.4047 | 24.0857 | 23.223 | 22.968 | 22.8775 | 21.4583 | 20.3096 | 18.1892 | 16.547 | 17.0857 | 16.7816 | 17.5933 | 18.5331 | 17.6936 | 18.6947 | 20.0324 | 21.7653 | 23.3233 | 24.5892 | 26.8551 | 25.631 | 25.7712
7 | 26.3967 | 28.387 | 28.2966 | 27.8906 | 26.5996 | 27.8956 | 26.3052 | 24.6081 | 23.9819 | 21.5715 | 20.0526 | 18.6139 | 17.9467 | 18.3547 | 16.3631 | 17.5342 | 19.3261 | 19.8674 | 24.8407 | 25.1816 | 25.0293 | 28.8997 | 28.6171 | 28.1718
8 | 28.4227 | 28.4089 | 28.2843 | 26.0381 | 26.5684 | 27.5174 | 26.7681 | 25.2695 | 26.4742 | 26.9226 | 23.5029 | 21.2098 | 18.5938 | 16.5576 | 17.5265 | 19.7702 | 21.7309 | 24.1081 | 27.1945 | 27.704 | 26.8377 | 27.1636 | 24.8489 | 24.6969
9 | 24.9067 | 24.5808 | 25.5226 | 24.7732 | 24.4027 | 27.0121 | 27.4509 | 28.6001 | 29.1658 | 28.7303 | 23.309 | 21.184 | 21.701 | 19.65 | 19.0668 | 17.6537 | 17.817 | 20.5416 | 22.6815 | 22.0152 | 22.8283 | 24.5397 | 27.2659 | 27.5771
10 | 27.4958 | 26.1967 | 26.645 | 25.1871 | 25.0378 | 27.0218 | 27.8743 | 25.8214 | 25.747 | 24.892 | 22.1327 | 19.8231 | 20.1767 | 21.1098 | 23.9775 | 23.7274 | 22.9746 | 26.4263 | 30.1184 | 29.7876 | 29.7249 | 31.0936 | 32.9155 | 31.1415
11 | 29.0767 | 28.4017 | 28.2142 | 26.9074 | 27.2018 | 29.7661 | 29.4111 | 29.1673 | 29.549 | 28.9824 | 26.9397 | 25.5028 | 21.203 | 20.5164 | 21.1463 | 20.877 | 21.3157 | 26.2266 | 28.3937 | 25.5463 | 24.9974 | 27.2505 | 27.5375 | 28.3835
12 | 28.5105 | 28.7891 | 28.2026 | 27.0218 | 26.4256 | 26.2032 | 26.3548 | 25.0773 | 24.511 | 23.982 | 21.7104 | 21.0013 | 18.6868 | 17.8447 | 19.8446 | 18.7853 | 18.6744 | 21.7528 | 22.7006 | 23.437 | 23.0046 | 20.9437 | 20.2013 | 22.8402
13 | 25.4005 | 26.8265 | 28.4313 | 28.0326 | 26.5049 | 28.5149 | 26.5416 | 24.5757 | 24.9386 | 23.51 | 21.8301 | 20.8107 | 18.6773 | 17.1778 | 20.308 | 21.2468 | 21.3778 | 20.959 | 24.087 | 26.5119 | 26.7036 | 26.5759 | 25.1481 | 25.7692
14 | 26.9644 | 25.9421 | 26.5149 | 27.9352 | 27.8323 | 26.3583 | 25.9718 | 26.3564 | 25.8508 | 25.3266 | 22.8528 | 21.1495 | 20.0851 | 17.6402 | 17.261 | 16.9709 | 17.415 | 18.2186 | 21.941 | 24.6975 | 24.5584 | 24.9481 | 25.6285 | 26.6999
15 | 28.2988 | 27.8993 | 28.3531 | 28.1272 | 26.952 | 26.5379 | 26.911 | 26.632 | 27.1069 | 27.5095 | 25.1879 | 24.1779 | 25.5106 | 24.7716 | 27.2174 | 26.064 | 26.5524 | 29.9603 | 32.0124 | 32.0075 | 32.1851 | 30.7229 | 29.962 | 28.003
16 | 28.1626 | 27.397 | 27.5404 | 28.7075 | 27.3169 | 27.8931 | 28.2852 | 25.445 | 25.7802 | 25.7233 | 23.745 | 22.2023 | 21.0889 | 21.4216 | 21.1976 | 19.9428 | 19.0801 | 19.2026 | 24.9706 | 24.526 | 23.9207 | 25.857 | 25.1543 | 24.2358
17 | 23.1648 | 22.9625 | 23.8728 | 24.8745 | 27.0107 | 28.3328 | 26.7249 | 26.6019 | 26.6479 | 26.0506 | 20.6919 | 18.0547 | 19.8543 | 20.5645 | 21.7502 | 19.393 | 16.9999 | 18.5973 | 22.0767 | 24.1409 | 26.4607 | 26.6047 | 27.4696 | 26.0402
18 | 26.2166 | 26.2317 | 26.0337 | 25.3855 | 24.7509 | 26.1731 | 24.7503 | 24.1412 | 24.0006 | 24.6892 | 21.8342 | 18.3196 | 18.2988 | 17.1648 | 15.9834 | 17.3807 | 20.0375 | 21.9917 | 26.3147 | 29.2108 | 30.524 | 29.3287 | 29.6715 | 30.2545
19 | 31.8015 | 32.8015 | 32.2362 | 30.2512 | 28.8247 | 30.5693 | 29.5429 | 27.6853 | 27.6068 | 24.335 | 22.5326 | 21.4232 | 18.8419 | 20.7554 | 22.0551 | 21.2206 | 22.0937 | 24.3054 | 28.7343 | 27.2807 | 30.0938 | 31.2302 | 29.2114 | 30.8322
20 | 29.4156 | 28.3579 | 27.1118 | 25.2797 | 24.1328 | 24.043 | 23.9087 | 22.4668 | 23.2221 | 23.5765 | 22.8473 | 22.5508 | 22.6409 | 22.6031 | 23.3839 | 24.1512 | 22.4767 | 25.5488 | 26.9736 | 26.4701 | 25.4627 | 25.9468 | 26.4884 | 27.7719
21 | 28.7751 | 29.5096 | 29.1349 | 27.857 | 27.2251 | 27.1676 | 27.7065 | 28.7381 | 29.2985 | 26.7024 | 24.4954 | 23.74 | 23.9723 | 23.9238 | 25.1903 | 23.2687 | 21.5163 | 24.2199 | 26.0078 | 26.1826 | 27.2003 | 25.7608 | 25.0956 | 26.4335
22 | 25.5574 | 24.8659 | 22.9864 | 24.4843 | 26.7685 | 30.2778 | 28.0623 | 25.6827 | 24.7767 | 21.9373 | 18.136 | 15.6211 | 17.9034 | 17.4521 | 17.9817 | 16.7397 | 17.4284 | 17.9813 | 21.7652 | 23.0718 | 25.7681 | 26.9689 | 26.6462 | 29.2247
23 | 31.4764 | 31.5425 | 29.4389 | 26.1575 | 26.0409 | 28.6349 | 27.2181 | 27.9939 | 27.7443 | 26.6634 | 24.4688 | 23.6325 | 24.4941 | 22.9285 | 19.5278 | 18.2432 | 20.0867 | 24.6883 | 30.6634 | 30.3331 | 29.654 | 29.2805 | 27.25 | 27.49
24 | 27.7014 | 26.6108 | 26.6028 | 28.9553 | 30.7788 | 33.0429 | 32.7609 | 31.8907 | 29.7974 | 26.6536 | 21.8298 | 20.6401 | 20.9269 | 18.9517 | 22.8985 | 23.5578 | 22.082 | 23.6829 | 25.4942 | 27.5544 | 29.3939 | 29.4714 | 27.8427 | 28.2697
25 | 27.6983 | 28.3659 | 27.6761 | 26.0812 | 24.4697 | 25.2575 | 23.8778 | 24.434 | 24.94 | 24.129 | 21.5693 | 17.7548 | 18.2985 | 18.9728 | 18.362 | 19.898 | 21.3201 | 22.6155 | 25.7396 | 25.5699 | 26.1777 | 26.5635 | 26.3988 | 26.912
26 | 27.1317 | 25.1338 | 24.0854 | 22.9822 | 22.1457 | 23.2164 | 21.5736 | 20.999 | 22.4176 | 23.4218 | 19.9051 | 19.6527 | 17.3664 | 18.6798 | 18.3962 | 19.8373 | 19.978 | 19.8413 | 24.2249 | 26.2464 | 25.6405 | 24.8146 | 24.4135 | 27.5364
27 | 28.5225 | 31.2703 | 32.6031 | 31.5747 | 30.6961 | 29.5729 | 26.8511 | 26.0842 | 25.2042 | 24.6786 | 22.2079 | 20.2476 | 18.9717 | 19.6043 | 20.9388 | 22.2512 | 24.8907 | 27.7802 | 27.9941 | 27.9732 | 29.2886 | 28.3928 | 26.2355 | 26.7368
28 | 26.161 | 25.5395 | 25.5832 | 25.6627 | 26.1715 | 26.4514 | 25.0915 | 24.7144 | 25.5861 | 26.9376 | 18.7022 | 17.8196 | 15.7496 | 18.117 | 20.6917 | 22.0449 | 22.1929 | 24.2077 | 27.525 | 29.1993 | 29.3286 | 29.1244 | 28.3694 | 26.8573
29 | 26.1517 | 24.515 | 24.6572 | 26.0613 | 25.2783 | 26.9637 | 27.5283 | 26.5251 | 25.3003 | 19.5111 | 14.4886 | 12.6108 | 14.8514 | 15.2805 | 17.5492 | 18.187 | 18.9896 | 22.101 | 24.8876 | 28.1062 | 29.0657 | 28.4383 | 27.7994 | 27.3455
30 | 26.4518 | 23.2359 | 23.0373 | 22.7435 | 22.5412 | 23.8696 | 24.7138 | 23.2859 | 24.7838 | 23.5499 | 18.0578 | 18.4975 | 21.8009 | 21.6585 | 21.3452 | 20.1822 | 20.6515 | 23.03 | 26.0925 | 23.6402 | 26.6678 | 27.6586 | 28.0163 | 30.1206
31 | 29.8585 | 28.5536 | 27.4559 | 25.3567 | 22.9023 | 24.0228 | 23.7848 | 21.7569 | 21.794 | 22.4588 | 21.2475 | 18.6136 | 17.5906 | 17.7527 | 16.86 | 15.6642 | 18.2841 | 22.7978 | 24.0926 | 23.5674 | 26.1217 | 22.4184 | 21.7378 | 19.815
32 | 18.1966 | 20.7007 | 22.7101 | 24.4445 | 23.7902 | 24.6673 | 22.7829 | 19.992 | 20.327 | 20.8485 | 19.2552 | 16.079 | 16.9221 | 15.6417 | 15.5244 | 17.9056 | 18.3189 | 20.6521 | 25.1234 | 27.4477 | 27.2956 | 26.5068 | 25.4405 | 24.9358
33 | 23.4921 | 24.5464 | 27.6464 | 28.851 | 30.1959 | 31.8538 | 30.4295 | 28.7381 | 29.6333 | 28.2653 | 22.4359 | 18.9773 | 16.6028 | 16.2261 | 14.8944 | 14.5673 | 15.4853 | 17.5926 | 19.5819 | 20.8851 | 23.1585 | 23.0592 | 21.923 | 20.8486
34 | 21.2498 | 22.9 | 22.7369 | 21.7822 | 22.8618 | 24.7439 | 25.5234 | 24.6456 | 23.8129 | 23.6319 | 21.282 | 19.1558 | 17.1399 | 14.5522 | 15.7242 | 14.8607 | 18.1849 | 21.4481 | 22.5968 | 22.2328 | 23.1406 | 20.4171 | 18.786 | 17.4017
35 | 16.0814 | 18.2139 | 20.2351 | 20.1378 | 19.4836 | 21.0391 | 20.4136 | 21.4455 | 23.2479 | 22.822 | 23.5184 | 23.0538 | 22.4987 | 20.7243 | 20.1417 | 18.8022 | 19.2296 | 23.6484 | 23.3592 | 22.5434 | 23.2707 | 22.0564 | 21.6869 | 23.2726
36 | 23.6334 | 22.9997 | 22.8579 | 22.1541 | 21.5452 | 23.3059 | 21.6137 | 21.0059 | 21.6218 | 21.7939 | 19.8907 | 17.9315 | 18.936 | 20.2386 | 18.6977 | 17.7326 | 18.4044 | 20.8969 | 21.2131 | 19.5231 | 20.8441 | 20.3868 | 19.0609 | 20.559
37 | 21.2452 | 21.7314 | 21.9132 | 22.5568 | 22.4556 | 24.0604 | 23.6238 | 24.0507 | 26.6778 | 28.1857 | 24.9547 | 21.4232 | 20.0083 | 20.1579 | 19.3893 | 18.0989 | 17.3648 | 22.3337 | 24.8002 | 25.4399 | 27.5507 | 26.8932 | 26.4158 | 25.396
38 | 25.938 | 26.7935 | 26.9922 | 26.2818 | 25.1963 | 24.841 | 23.1419 | 21.6392 | 23.1041 | 21.9512 | 20.2929 | 19.8878 | 21.1087 | 19.1281 | 19.592 | 21.3639 | 21.0006 | 21.742 | 25.2019 | 28.0966 | 29.4874 | 30.3275 | 30.4017 | 28.3727
39 | 27.1867 | 26.8436 | 26.5399 | 24.8296 | 24.8851 | 24.9722 | 23.7355 | 23.4033 | 22.8998 | 20.8787 | 18.6529 | 20.239 | 21.2825 | 21.0702 | 22.8733 | 20.1071 | 19.1975 | 17.6744 | 19.8864 | 20.4381 | 19.2524 | 18.8719 | 18.9555 | 20.1313
40 | 19.8596 | 20.3839 | 21.807 | 21.0323 | 21.9898 | 23.6985 | 23.5984 | 23.4256 | 24.1574 | 23.5481 | 19.2674 | 19.66 | 18.4085 | 18.8906 | 18.8349 | 19.1727 | 20.054 | 23.5518 | 26.3071 | 28.5148 | 31.3309 | 29.1684 | 27.1639 | 27.084
41 | 27.1958 | 28.1368 | 26.7766 | 25.4425 | 24.5846 | 25.6649 | 25.2384 | 23.792 | 22.8031 | 21.679 | 19.6681 | 18.182 | 17.4011 | 20.3754 | 21.0253 | 19.283 | 18.6299 | 19.1694 | 22.8692 | 21.0856 | 22.1385 | 20.0543 | 20.4937 | 21.2479
42 | 20.4616 | 20.565 | 20.5065 | 18.2809 | 17.1949 | 19.8767 | 22.0314 | 23.4868 | 24.0424 | 23.3688 | 21.0322 | 18.4242 | 16.5718 | 15.2844 | 17.7346 | 18.7594 | 19.4142 | 20.1354 | 22.6033 | 22.2249 | 19.1212 | 18.5526 | 20.757 | 21.0242
43 | 19.5795 | 22.5978 | 23.2363 | 20.991 | 19.1696 | 22.0649 | 21.8548 | 21.5401 | 21.498 | 21.2616 | 18.1679 | 14.574 | 15.0104 | 17.4242 | 18.9271 | 19.0448 | 19.7249 | 20.1802 | 20.3702 | 21.4221 | 23.4058 | 23.8536 | 26.4489 | 29.6004
44 | 29.8929 | 31.1678 | 32.9241 | 30.8822 | 29.1082 | 29.7555 | 29.1259 | 29.9911 | 29.6453 | 27.8644 | 23.778 | 21.186 | 19.7857 | 21.4274 | 21.8646 | 22.787 | 24.1609 | 24.5992 | 27.1765 | 29.3728 | 32.3122 | 31.3717 | 29.5416 | 31.3524
45 | 30.6212 | 30.6703 | 30.8097 | 28.9457 | 27.9939 | 29.1763 | 30.3796 | 28.4105 | 29.1508 | 27.3505 | 26.9784 | 25.4915 | 24.8792 | 25.9423 | 27.3633 | 26.5748 | 27.1348 | 29.7103 | 26.6159 | 25.1798 | 27.5986 | 28.8021 | 27.6367 | 27.3594
46 | 25.832 | 26.1684 | 27.6871 | 25.5607 | 24.2042 | 24.1395 | 22.9088 | 21.6916 | 20.7787 | 20.1425 | 18.6635 | 18.7097 | 17.6336 | 16.5668 | 17.0299 | 16.777 | 17.4028 | 19.6575 | 21.2942 | 21.3215 | 22.132 | 22.5557 | 23.661 | 24.309
47 | 24.5179 | 25.0952 | 25.9788 | 24.6379 | 23.3613 | 21.9001 | 19.8279 | 19.6242 | 19.5577 | 19.7392 | 17.8655 | 17.4308 | 16.2627 | 17.9797 | 17.1712 | 16.287 | 17.4099 | 22.0375 | 24.9477 | 26.8475 | 29.9898 | 30.0337 | 26.9546 | 29.2727
48 | 29.4451 | 30.3309 | 30.5042 | 31.7481 | 31.5525 | 29.4202 | 24.4895 | 22.8383 | 22.7941 | 20.2068 | 17.3106 | 15.4638 | 15.5665 | 15.35 | 17.0096 | 17.5582 | 19.2308 | 22.7543 | 26.417 | 28.903 | 29.4148 | 28.4938 | 27.3552 | 27.361
49 | 26.5424 | 26.2183 | 27.5235 | 25.6398 | 24.8647 | 24.5119 | 24.0186 | 24.457 | 23.9104 | 21.2825 | 20.7153 | 19.7969 | 19.6544 | 21.0157 | 21.3004 | 22.4428 | 23.9604 | 24.297 | 25.5627 | 25.6663 | 31.5617 | 29.3492 | 24.4406 | 25.6232
50 | 23.7239 | 24.5266 | 25.205 | 25.311 | 25.8971 | 26.4853 | 25.0954 | 25.6237 | 26.8195 | 25.9026 | 21.7972 | 22.758 | 24.7697 | 25.794 | 27.9899 | 28.6128 | 27.9852 | 29.4811 | 27.0625 | 29.0257 | 29.9997 | 29.8761 | 29.6658 | 30.1016
51 | 29.8017 | 31.0564 | 30.2309 | 29.1183 | 28.2673 | 27.9842 | 25.721 | 24.1271 | 26.8196 | 23.1195 | 20.659 | 18.9584 | 18.5318 | 20.0634 | 21.4223 | 21.361 | 22.298 | 26.3392 | 26.0386 | 24.6239 | 27.9166 | 26.4164 | 25.0951 | 26.5094
52 | 25.8932 | 26.101 | 25.0309 | 22.8772 | 20.7161 | 22.2272 | 23.8671 | 23.1877 | 23.647 | 22.9464 | 23.5142 | 23.7421 | 23.1446 | 23.4726 | 24.6187 | 23.8691 | 25.8907 | 25.8722 | 25.8401 | 23.5604 | 22.4838 | 22.3979 | 20.0404 | 22.7789
53 | 25.1077 | 27.1094 | 29.109 | 29.749 | 30.2282 | 31.8773 | 32.7402 | 32.4214 | 30.54 | 26.2804 | 23.5351 | 23.0478 | 19.9172 | 20.7474 | 22.7769 | 22.6411 | 23.6839 | 23.7407 | 24.1739 | 28.1908 | 30.4682 | 32.4655 | 31.0804 | 28.1713
54 | 25.3694 | 25.651 | 25.8676 | 27.6371 | 29.9976 | 30.5544 | 28.0154 | 25.5437 | 25.1638 | 24.9971 | 26.2545 | 25.0416 | 22.7879 | 21.7398 | 23.0322 | 25.8306 | 26.8516 | 27.6587 | 26.9019 | 28.716 | 29.3952 | 27.1699 | 25.7859 | 26.781
55 | 25.957 | 25.3448 | 24.6232 | 23.7248 | 23.627 | 27.7329 | 28.8516 | 26.7322 | 25.4421 | 23.541 | 23.0689 | 19.4941 | 18.7486 | 20.3837 | 21.8409 | 23.9235 | 26.2098 | 27.7184 | 30.0135 | 30.7723 | 30.2908 | 29.4094 | 29.7241 | 29.2376
56 | 25.9513 | 26.0324 | 26.2818 | 26.3562 | 26.4156 | 27.5515 | 27.796 | 26.8311 | 27.1115 | 24.3642 | 23.1863 | 23.6281 | 22.8111 | 22.1023 | 20.8931 | 22.4987 | 25.6932 | 25.6259 | 24.0212 | 23.9185 | 26.3507 | 26.1764 | 27.1027 | 28.8253
57 | 29.2682 | 26.5128 | 25.0039 | 21.8087 | 20.7305 | 21.6537 | 22.0571 | 21.5897 | 23.0424 | 22.7344 | 23.3453 | 21.25 | 19.7219 | 20.5628 | 21.5594 | 22.8162 | 26.4748 | 30.2441 | 26.7337 | 30.5058 | 31.6232 | 26.9856 | 28.3972 | 27.7997
58 | 25.6043 | 25.6196 | 25.7451 | 25.3291 | 23.8847 | 24.8086 | 24.5151 | 24.0864 | 24.1541 | 23.3053 | 23.4151 | 22.0492 | 19.1382 | 17.5825 | 17.4961 | 17.8737 | 18.8361 | 23.5738 | 26.9334 | 29.8794 | 27.2025 | 26.5365 | 26.2069 | 26.0301
59 | 23.3002 | 22.279 | 22.5468 | 23.0616 | 21.9606 | 22.2075 | 20.7046 | 20.613 | 21.3596 | 18.6973 | 18.3775 | 18.9667 | 18.0654 | 18.8305 | 20.1387 | 21.9558 | 22.1249 | 23.1007 | 24.2953 | 24.2536 | 24.1775 | 23.701 | 23.2915 | 24.5521
60 | 26.3437 | 25.7961 | 25.7172 | 24.4192 | 23.3192 | 23.5106 | 23.6148 | 24.3988 | 24.4355 | 21.2596 | 18.8782 | 17.7685 | 17.1072 | 17.9077 | 20.1462 | 22.5949 | 24.074 | 25.0212 | 26.8474 | 26.8671 | 28.2935 | 29.8245 | 29.7141 | 28.4511
61 | 24.1138 | 21.6391 | 21.4794 | 20.7045 | 21.1387 | 20.7342 | 18.4821 | 16.157 | 17.5151 | 16.8946 | 16.5195 | 19.0084 | 18.9081 | 17.989 | 17.885 | 18.424 | 20.1518 | 21.8358 | 23.7437 | 24.4604 | 26.7822 | 26.0453 | 24.991 | 24.9251
62 | 24.8522 | 26.2839 | 25.8813 | 23.8464 | 24.8102 | 26.4404 | 25.9808 | 25.8313 | 27.0463 | 25.3754 | 26.9182 | 26.2927 | 24.3312 | 24.8955 | 28.275 | 26.129 | 27.593 | 29.1341 | 27.7153 | 29.3878 | 30.8263 | 30.7115 | 27.3201 | 28.8427
63 | 30.0701 | 29.4816 | 33.0569 | 31.9588 | 30.4699 | 30.6764 | 29.1135 | 27.9461 | 28.1346 | 25.4457 | 22.8379 | 21.7341 | 21.1107 | 20.5381 | 21.7937 | 23.5054 | 28.1404 | 26.9617 | 28.7165 | 24.2361 | 27.4744 | 25.1578 | 22.116 | 20.7075
64 | 16.9366 | 19.3545 | 21.0317 | 22.8661 | 22.5488 | 22.2425 | 19.2368 | 19.0608 | 19.6546 | 18.1123 | 19.9585 | 21.1478 | 21.2514 | 22.4369 | 22.5235 | 20.5826 | 23.1083 | 25.6566 | 27.317 | 29.1927 | 28.07 | 28.1321 | 26.74 | 25.2705
65 | 26.5826 | 24.0651 | 26.05 | 27.8343 | 28.0984 | 29.5907 | 29.6137 | 28.335 | 28.4533 | 26.295 | 23.8273 | 22.95 | 23.0258 | 24.7048 | 26.6121 | 25.8791 | 29.7779 | 27.5466 | 27.8435 | 28.2372 | 28.739 | 26.7709 | 23.8399 | 24.4506
66 | 26.0493 | 26.8841 | 26.4023 | 25.1344 | 23.9043 | 25.1018 | 25.5603 | 23.928 | 24.3327 | 23.102 | 24.5962 | 24.0616 | 24.3689 | 26.2045 | 28.4009 | 28.4535 | 31.3178 | 30.3126 | 30.2108 | 26.0924 | 26.0586 | 26.4002 | 27.6567 | 29.0109
67 | 30.9871 | 30.5697 | 27.7954 | 22.1668 | 21.1511 | 22.5976 | 21.1986 | 19.9578 | 18.6755 | 17.5588 | 19.2649 | 20.0179 | 18.0717 | 17.3118 | 20.0525 | 22.1165 | 21.8213 | 20.6953 | 18.5736 | 23.0229 | 24.9351 | 25.4346 | 23.1313 | 21.6219
68 | 22.0492 | 23.243 | 24.7003 | 24.1062 | 24.4379 | 26.7229 | 28.0009 | 26.1757 | 24.864 | 21.8837 | 22.0327 | 21.6333 | 18.196 | 16.6094 | 17.3647 | 18.8747 | 23.2696 | 24.0017 | 25.5608 | 28.3633 | 26.4052 | 28.7524 | 31.7888 | 33.6274
69 | 32.9002 | 33.4647 | 31.7816 | 29.3087 | 28.823 | 27.5823 | 26.36 | 25.8233 | 25.6611 | 22.161 | 18.797 | 17.3892 | 16.5673 | 17.33 | 17.1366 | 16.7603 | 19.7923 | 23.9206 | 25.5989 | 25.9577 | 28.7974 | 29.7775 | 27.9066 | 26.7212
70 | 26.1923 | 23.7119 | 22.2797 | 20.607 | 19.9123 | 21.5937 | 21.5728 | 21.8808 | 23.5641 | 21.7041 | 22.8706 | 24.7806 | 23.65 | 22.5884 | 23.6283 | 26.2502 | 25.8072 | 28.1669 | 31.8724 | 35.2626 | 35.1976 | 30.1723 | 27.1453 | 27.4007
71 | 26.7091 | 25.7565 | 26.1331 | 26.0642 | 28.9565 | 30.9869 | 31.7991 | 30.1543 | 28.9426 | 25.1513 | 25.3678 | 27.5712 | 23.2979 | 21.9213 | 20.1873 | 24.1866 | 25.4733 | 24.6462 | 23.6404 | 25.6698 | 26.2453 | 25.7156 | 22.8744 | 21.021
72 | 20.9532 | 22.1522 | 22.7502 | 21.8988 | 22.1384 | 23.8044 | 22.2505 | 19.7388 | 18.7266 | 16.1215 | 15.4797 | 16.0504 | 15.6618 | 18.7211 | 19.4839 | 18.846 | 23.2056 | 22.854 | 21.9146 | 22.2441 | 23.1672 | 23.6986 | 25.1598 | 24.896
73 | 27.1938 | 26.9354 | 25.3413 | 22.6364 | 24.5589 | 26.225 | 24.9224 | 21.3932 | 20.9345 | 17.1558 | 17.6089 | 19.3005 | 22.1762 | 25.1849 | 23.5932 | 24.0397 | 24.8968 | 28.9864 | 31.9932 | 29.6314 | 32.5988 | 30.2477 | 28.9973 | 29.7229
74 | 28.632 | 27.645 | 27.3482 | 25.5441 | 24.468 | 23.9533 | 22.8225 | 20.7125 | 18.2502 | 18.4191 | 18.5103 | 17.2767 | 17.8516 | 19.4159 | 21.7318 | 23.1875 | 23.4497 | 22.3399 | 26.2896 | 28.8484 | 29.1285 | 29.6249 | 29.6436 | 29.392
75 | 29.3098 | 28.3984 | 29.1027 | 29.0336 | 27.9563 | 28.1738 | 26.7601 | 24.1739 | 24.7494 | 25.3231 | 25.7657 | 29.5036 | 30.3293 | 29.1915 | 26.5837 | 26.7534 | 28.4204 | 27.1777 | 26.5806 | 25.8187 | 29.1488 | 29.3789 | 27.3514 | 26.7755
76 | 28.7617 | 26.1669 | 24.5172 | 24.7353 | 26.2001 | 26.8538 | 26.4571 | 26.4295 | 25.2314 | 24.2246 | 24.4185 | 24.4322 | 25.9658 | 26.4465 | 26.1385 | 24.5451 | 28.6171 | 25.5946 | 28.4686 | 27.3076 | 26.7202 | 30.1655 | 30.2398 | 26.037
77 | 21.4519 | 18.6867 | 19.7786 | 19.9689 | 20.8708 | 20.7119 | 18.0616 | 15.5018 | 14.9362 | 15.8291 | 20.6626 | 21.6936 | 22.0515 | 22.8425 | 24.3124 | 26.895 | 29.5219 | 28.2324 | 26.207 | 24.7867 | 23.9819 | 23.3473 | 24.3543 | 23.9786
78 | 23.8026 | 25.0184 | 24.1332 | 23.6296 | 24.1489 | 24.7209 | 23.8343 | 23.7003 | 23.421 | 21.1343 | 20.7148 | 19.5212 | 20.0262 | 21.5815 | 21.9362 | 21.9889 | 24.1224 | 25.0396 | 23.3896 | 24.2432 | 27.9193 | 27.5216 | 26.9089 | 23.4503
79 | 23.6238 | 23.4446 | 23.8261 | 24.1378 | 23.3622 | 24.0997 | 22.6165 | 22.0545 | 21.1861 | 17.0834 | 17.0344 | 17.3146 | 18.0483 | 18.6049 | 19.4848 | 21.2833 | 23.6587 | 20.9128 | 24.0287 | 25.2546 | 28.0704 | 27.1554 | 25.7795 | 27.8996
80 | 25.2675 | 24.4464 | 22.9851 | 21.4715 | 19.7251 | 21.0579 | 21.0008 | 19.4 | 18.2813 | 16.1544 | 16.0426 | 17.6683 | 17.7015 | 19.2506 | 25.8554 | 26.7321 | 29.4095 | 29.0851 | 30.7013 | 32.6692 | 29.9462 | 26.9416 | 27.182 | 26.1234
81 | 26.5321 | 25.5895 | 23.0971 | 22.4484 | 23.8021 | 25.5204 | 23.7514 | 21.599 | 20.0667 | 19.9022 | 17.7962 | 18.4258 | 18.0618 | 16.7449 | 18.8156 | 20.1702 | 23.117 | 23.1134 | 25.4131 | 26.2209 | 26.8895 | 28.6645 | 28.0641 | 27.6082
82 | 30.8132 | 26.567 | 26.1198 | 25.9679 | 24.4058 | 23.0546 | 22.5079 | 22.8925 | 22.3553 | 19.2942 | 18.3356 | 18.2898 | 19.0935 | 19.7192 | 22.4538 | 26.7326 | 27.2869 | 32.4363 | 31.3068 | 29.7576 | 28.8853 | 29.2043 | 30.8926 | 31.5074
83 | 32.4912 | 30.9458 | 31.8536 | 30.9561 | 29.737 | 29.4982 | 28.6515 | 27.1343 | 25.5535 | 24.24 | 22.1483 | 21.0351 | 23.3691 | 24.2251 | 26.1506 | 24.842 | 22.9902 | 25.6127 | 27.9554 | 28.0418 | 27.2034 | 27.3397 | 25.907 | 26.16
84 | 26.3758 | 24.5173 | 23.733 | 21.1168 | 20.6903 | 20.692 | 20.4853 | 19.8821 | 19.2352 | 19.2763 | 21.3884 | 20.1321 | 21.4354 | 22.5456 | 23.7118 | 25.7509 | 28.1538 | 29.783 | 30.2542 | 30.9143 | 31.758 | 29.2423 | 31.9952 | 30.1358
85 | 28.2584 | 26.4796 | 28.1122 | 27.2975 | 27.9289 | 28.7599 | 28.258 | 29.3959 | 28.669 | 25.3172 | 23.8055 | 22.0176 | 24.084 | 25.162 | 29.4722 | 27.7617 | 27.2755 | 27.3982 | 30.2125 | 30.1152 | 30.5131 | 30.0642 | 30.0939 | 29.0795
86 | 30.7464 | 29.0008 | 29.7309 | 26.5255 | 27.3574 | 26.7736 | 24.7077 | 24.4351 | 22.6292 | 21.6174 | 24.3271 | 22.3943 | 22.868 | 26.1872 | 27.5388 | 29.6083 | 30.838 | 34.1324 | 32.1783 | 32.1469 | 30.8269 | 30.9308 | 30.6769 | 29.0179
87 | 28.1735 | 26.6897 | 27.491 | 26.241 | 27.7876 | 29.7272 | 27.8902 | 26.7286 | 23.4894 | 24.9627 | 28.1611 | 27.3092 | 24.7922 | 27.3627 | 29.0051 | 32.3769 | 30.7438 | 29.9373 | 29.5186 | 31.9763 | 28.4378 | 28.9083 | 28.8122 | 25.3595
88 | 27.7508 | 27.6966 | 27.4676 | 26.1973 | 25.7678 | 26.1818 | 26.0311 | 24.4214 | 21.6947 | 21.5944 | 21.6498 | 21.3976 | 20.5022 | 22.6295 | 25.4397 | 27.3843 | 28.273 | 26.5843 | 27.7678 | 25.748 | 25.897 | 25.5473 | 26.0359 | 24.673
89 | 24.9709 | 23.7912 | 23.2296 | 24.2752 | 24.3638 | 24.4606 | 23.9969 | 23.7173 | 20.936 | 18.3402 | 17.8041 | 17.829 | 18.635 | 20.4987 | 23.2642 | 25.6607 | 27.3043 | 25.3103 | 27.1048 | 25.3056 | 24.5603 | 27.2829 | 27.9095 | 31.1517
90 | 30.2727 | 26.6073 | 25.4919 | 25.8884 | 26.278 | 25.8905 | 26.0674 | 25.7122 | 22.7552 | 20.4486 | 19.7839 | 19.5823 | 21.9466 | 21.3801 | 20.5404 | 21.8211 | 24.6104 | 25.5035 | 24.7193 | 29.4108 | 28.0036 | 25.7891 | 28.6852 | 28.4112
91 | 27.7007 | 29.3221 | 29.1884 | 28.1125 | 26.1724 | 27.4706 | 27.5085 | 29.2889 | 28.3979 | 25.1818 | 23.4322 | 23.3206 | 25.6754 | 27.0012 | 26.1317 | 27.4514 | 30.5453 | 33.6853 | 31.957 | 32.5155 | 32.199 | 32.1092 | 30.137 | 30.6369
92 | 30.3446 | 31.2746 | 32.6 | 29.0692 | 28.4996 | 31.0658 | 31.2377 | 30.0227 | 27.5738 | 26.7704 | 24.8215 | 25.9356 | 24.8586 | 26.0063 | 27.0754 | 28.3898 | 28.8719 | 25.2694 | 27.7415 | 27.5382 | 29.516 | 29.9749 | 31.4287 | 29.9447
93 | 30.2495 | 27.7333 | 29.1344 | 27.1882 | 27.2348 | 26.1188 | 27.1924 | 25.5724 | 23.5705 | 23.4956 | 22.0238 | 21.6309 | 21.8729 | 22.2394 | 25.2616 | 25.092 | 25.839 | 24.8467 | 26.237 | 29.5415 | 28.8648 | 27.9273 | 25.243 | 25.8105
94 | 25.4785 | 25.0424 | 24.1194 | 21.2401 | 21.4551 | 23.6775 | 24.1856 | 23.9686 | 21.8475 | 21.8137 | 19.993 | 22.1743 | 23.5519 | 24.2872 | 25.9529 | 26.7829 | 23.2652 | 29.1715 | 27.7883 | 28.9521 | 33.0521 | 37.4554 | 35.7445 | 34.171
95 | 33.0162 | 31.4495 | 30.6821 | 30.1298 | 29.8515 | 28.4303 | 28.5564 | 27.9596 | 25.5093 | 26.1468 | 27.1637 | 25.454 | 20.7316 | 20.1082 | 21.074 | 24.2338 | 25.701 | 23.2609 | 26.1202 | 27.5314 | 31.0528 | 30.0683 | 28.7702 | 29.9017
96 | 31.2906 | 30.7193 | 29.8091 | 28.3783 | 27.3531 | 27.8681 | 27.1237 | 25.8271 | 22.9185 | 20.3643 | 19.5335 | 21.731 | 22.5031 | 23.6807 | 27.8304 | 26.9347 | 25.7735 | 26.7801 | 26.9175 | 31.2015 | 32.0104 | 32.6095 | 31.1591 | 32.6294
97 | 31.7989 | 30.5108 | 29.1505 | 25.9802 | 27.2959 | 29.216 | 27.2229 | 26.4441 | 23.9804 | 21.5083 | 20.2005 | 21.2724 | 22.9245 | 24.0182 | 30.1045 | 29.8362 | 28.8912 | 32.8739 | 30.2503 | 28.854 | 29.6379 | 30.0376 | 27.951 | 27.7735
98 | 24.2707 | 23.911 | 22.7398 | 19.6187 | 18.9518 | 19.3741 | 20.3743 | 20.724 | 18.7054 | 20.9004 | 21.861 | 19.7537 | 21.2694 | 24.0408 | 21.8881 | 23.5022 | 20.5254 | 20.6305 | 24.2546 | 27.3161 | 25.2659 | 28.5341 | 28.7814 | 29.2822
99 | 30.8036 | 28.739 | 28.6801 | 29.7686 | 27.7199 | 26.1643 | 26.8428 | 28.2349 | 23.6926 | 21.9408 | 20.4263 | 19.7777 | 20.5566 | 20.7285 | 21.1782 | 25.3124 | 27.0047 | 26.2887 | 29.3431 | 30.6838 | 29.5102 | 30.0615 | 29.2193 | 26.2111
100 | 27.2437 | 28.3189 | 27.7611 | 25.7665 | 22.5762 | 20.6904 | 19.2459 | 20.8451 | 20.0631 | 19.9471 | 19.243 | 18.9533 | 20.2023 | 23.06 | 24.881 | 26.4737 | 28.4796 | 26.6627 | 27.8192 | 28.8263 | 28.058 | 28.024 | 27.4172 | 24.5609
101 | 26.3382 | 23.3202 | 22.0503 | 24.3999 | 22.3134 | 21.9897 | 21.4266 | 21.9529 | 20.3435 | 17.8529 | 21.0581 | 18.7716 | 20.6845 | 25.1332 | 28.3295 | 29.0611 | 29.2595 | 26.0199 | 29.5192 | 31.1799 | 30.4976 | 31.4791 | 31.5854 | 26.7152
102 | 25.9399 | 24.6532 | 22.9913 | 19.9704 | 19.0054 | 18.6329 | 18.6285 | 19.2261 | 16.1153 | 16.0782 | 15.9745 | 16.6257 | 18.133 | 23.198 | 22.3291 | 23.9463 | 23.0253 | 26.1172 | 27.5791 | 31.6805 | 27.2385 | 28.5581 | 29.0053 | 28.4858
103 | 27.5758 | 25.397 | 23.7464 | 23.1079 | 24.1896 | 25.2335 | 24.0695 | 23.9767 | 21.5438 | 22.9397 | 21.9239 | 23.1172 | 23.2636 | 22.155 | 22.7212 | 21.1125 | 22.4416 | 25.2147 | 28.1279 | 28.6883 | 29.8083 | 33.6577 | 38.1656 | 34.8215
104 | 30.9492 | 30.2175 | 31.12 | 29.2407 | 28.9046 | 27.7937 | 27.5035 | 26.5901 | 25.6565 | 26.242 | 25.729 | 26.0039 | 25.5145 | 25.7972 | 27.1478 | 27.1244 | 29.4347 | 26.838 | 29.0182 | 33.9733 | 33.5255 | 33.3009 | 32.2131 | 32.8521
105 | 33.0328 | 28.1387 | 27.9924 | 27.9814 | 26.4368 | 25.4628 | 24.0412 | 19.2928 | 16.2993 | 15.4023 | 15.5396 | 16.5328 | 18.4409 | 19.8831 | 22.1487 | 23.0379 | 21.918 | 25.4787 | 27.4935 | 30.0686 | 23.4732 | 26.8712 | 28.7469 | 25.9645
106 | 25.4318 | 24.6292 | 27.8142 | 27.9068 | 25.3799 | 24.3833 | 24.4478 | 23.9037 | 17.4459 | 15.9696 | 18.5659 | 17.6715 | 20.5774 | 18.3589 | 22.8641 | 24.2322 | 22.2598 | 21.2258 | 26.1407 | 25.2112 | 29.2606 | 27.8628 | 26.8339 | 25.5161
107 | 23.8783 | 21.883 | 23.1149 | 22.0698 | 22.7002 | 23.1506 | 22.8965 | 21.1868 | 16.7058 | 16.152 | 17.23 | 16.9795 | 18.5931 | 19.9589 | 19.6545 | 23.4673 | 23.8747 | 26.2593 | 28.2302 | 30.2517 | 29.6869 | 30.7378 | 31.3301 | 27.2235
108 | 29.2207 | 29.1912 | 30.2291 | 27.3163 | 29.2225 | 27.0379 | 27.1183 | 26.9958 | 24.2236 | 21.4885 | 22.08 | 23.4334 | 23.1334 | 23.2842 | 26.7379 | 23.1142 | 25.7263 | 27.0571 | 30.0809 | 30.7648 | 30.3278 | 26.9576 | 31.1329 | 32.3885
109 | 34.9097 | 31.899 | 30.9326 | 29.2985 | 27.418 | 26.2933 | 27.2911 | 25.1999 | 22.1007 | 19.3621 | 16.7224 | 18.7129 | 18.5918 | 18.3309 | 20.3909 | 22.0637 | 22.9678 | 26.167 | 28.0292 | 25.8734 | 25.4515 | 27.2164 | 26.8178 | 25.2467
110 | 23.6083 | 23.6341 | 23.2706 | 21.1265 | 20.7027 | 19.22 | 19.7609 | 16.887 | 12.6962 | 11.9709 | 12.315 | 12.1399 | 14.3263 | 18.9851 | 18.8857 | 23.2719 | 22.2878 | 26.7057 | 26.8475 | 28.716 | 29.9354 | 27.9939 | 26.742 | 26.3941
111 | 26.2684 | 24.8938 | 25.1956 | 24.8055 | 22.751 | 21.2806 | 23.8359 | 23.7681 | 16.2409 | 14.4853 | 13.342 | 16.3198 | 18.9102 | 21.4884 | 23.1895 | 27.1854 | 25.0596 | 26.3394 | 27.8401 | 33.9304 | 29.4023 | 29.2391 | 27.0558 | 28.676
112 | 26.3448 | 23.0976 | 21.8865 | 18.6738 | 17.5859 | 18.238 | 19.3676 | 20.7823 | 20.0513 | 20.8096 | 19.2677 | 19.6344 | 20.3439 | 23.1491 | 22.7353 | 26.0556 | 22.0277 | 25.1661 | 27.4508 | 29.1386 | 30.2142 | 28.7808 | 30.9527 | 27.945
113 | 28.8587 | 28.8529 | 27.1745 | 24.2011 | 24.6555 | 25.6177 | 27.1515 | 25.3055 | 21.4636 | 21.4814 | 19.6282 | 20.8737 | 22.3514 | 25.3693 | 23.4484 | 26.3848 | 27.6783 | 30.3576 | 30.6258 | 35.4236 | 36.212 | 33.5151 | 30.6914 | 31.4546
114 | 32.7331 | 30.9433 | 29.8699 | 29.8489 | 29.9656 | 29.3157 | 29.404 | 28.935 | 25.5476 | 24.0135 | 24.6358 | 24.8804 | 28.2083 | 27.9357 | 29.6168 | 31.6299 | 32.8793 | 33.5874 | 28.9263 | 31.2585 | 32.7215 | 33.7114 | 31.0778 | 29.0773
115 | 32.9976 | 33.9005 | 33.6991 | 32.0916 | 30.4568 | 27.5833 | 27.9711 | 25.228 | 22.1108 | 21.1774 | 18.5151 | 20.3381 | 22.668 | 22.0877 | 23.8778 | 26.2659 | 25.012 | 29.4488 | 27.0248 | 27.1564 | 28.3843 | 27.6009 | 26.9855 | 28.1694
116 | 27.1688 | 24.9241 | 25.6566 | 23.8451 | 24.5168 | 22.9699 | 23.1049 | 21.5128 | 17.636 | 18.7167 | 20.0831 | 19.4452 | 21.3247 | 21.1571 | 21.6843 | 24.1615 | 21.2199 | 27.4479 | 27.3198 | 28.6633 | 28.6759 | 30.1927 | 31.1779 | 28.5749
117 | 26.6175 | 24.1588 | 21.0782 | 18.7867 | 18.5059 | 19.4922 | 20.0918 | 17.4735 | 17.5696 | 16.5573 | 17.1211 | 17.0974 | 19.0907 | 22.5492 | 27.8699 | 28.2229 | 26.2852 | 30.429 | 28.9995 | 29.8664 | 30.4535 | 30.2987 | 27.6299 | 28.6781
118 | 29.2319 | 29.522 | 28.4501 | 25.7374 | 25.3208 | 22.3072 | 23.6581 | 22.7766 | 20.3249 | 19.9703 | 19.9443 | 21.9756 | 22.0478 | 21.6081 | 26.8933 | 27.5884 | 29.4013 | 28.9349 | 28.5466 | 26.4056 | 32.6004 | 32.9218 | 33.2106 | 32.3548
119 | 31.4918 | 27.0772 | 25.1967 | 23.6412 | 21.8752 | 21.4284 | 21.7698 | 20.2775 | 21.407 | 22.5986 | 22.8318 | 22.4962 | 22.0479 | 21.5113 | 24.0918 | 23.4686 | 21.5897 | 25.1173 | 30.088 | 26.7924 | 29.9361 | 30.5456 | 29.0959 | 28.5138
120 | 28.3519 | 23.8623 | 23.8625 | 25.3768 | 22.57 | 23.218 | 23.9213 | 21.319 | 17.9536 | 21.4598 | 24.937 | 24.5743 | 26.0936 | 28.0023 | 29.1506 | 33.508 | 32.9135 | 31.5512 | 30.8028 | 27.046 | 27.7337 | 28.3234 | 24.8771 | 24.1785
121 | 23.7848 | 19.6606 | 19.1594 | 19.4446 | 18.7321 | 19.2103 | 17.3574 | 16.8332 | 16.5629 | 17.5591 | 16.342 | 18.9325 | 22.5237 | 23.2675 | 26.8486 | 27.2325 | 23.6248 | 29.0357 | 31.7096 | 34.9431 | 26.9993 | 21.7129 | 21.4399 | 23.3018
122 | 19.7791 | 18.6416 | 21.7256 | 18.9561 | 16.863 | 15.374 | 18.3481 | 18.3522 | 16.9278 | 15.7529 | 13.7544 | 15.1776 | 21.3371 | 19.4072 | 22.8388 | 24.1822 | 22.7513 | 21.2374 | 23.4789 | 26.1568 | 25.8941 | 24.1246 | 26.4025 | 25.1055
123 | 21.7454 | 21.1868 | 22.239 | 23.918 | 24.9778 | 23.1386 | 22.2689 | 20.6159 | 17.086 | 16.3786 | 15.2057 | 14.6501 | 16.4962 | 19.7495 | 20.9877 | 24.1464 | 23.433 | 24.7618 | 23.3696 | 29.2079 | 29.7168 | 31.8858 | 28.4414 | 27.1791
124 | 24.9764 | 24.4745 | 23.0216 | 21.1809 | 21.5412 | 21.3112 | 21.6409 | 18.5237 | 15.4744 | 15.2125 | 15.3896 | 16.0311 | 19.2686 | 18.2418 | 18.8643 | 22.4934 | 25.1103 | 28.4554 | 29.0875 | 28.5144 | 31.6699 | 29.5944 | 29.9901 | 27.7587
125 | 24.179 | 21.8754 | 22.8411 | 20.9717 | 21.1102 | 20.0502 | 20.0998 | 19.4766 | 17.6785 | 17.9379 | 19.8037 | 20.3863 | 20.7114 | 21.9606 | 25.2834 | 25.1049 | 25.3252 | 30.0703 | 27.0981 | 28.9952 | 30.5601 | 28.7975 | 27.8229 | 29.031
126 | 28.3496 | 26.8953 | 24.7182 | 25.6255 | 26.2965 | 27.0696 | 28.6829 | 24.7307 | 19.8665 | 18.5675 | 17.15 | 17.1867 | 21.5466 | 24.4784 | 26.4732 | 28.4785 | 27.9593 | 27.2802 | 34.1211 | 34.1091 | 36.0695 | 31.0142 | 30.8765 | 31.3433
127 | 30.3041 | 27.24 | 27.345 | 26.1026 | 25.9967 | 23.192 | 21.2728 | 17.1337 | 13.1648 | 13.2521 | 14.4698 | 15.7052 | 20.2204 | 22.6399 | 25.3008 | 27.1726 | 27.8136 | 30.3999 | 32.6021 | 31.6133 | 34.4103 | 33.5024 | 34.8908 | 35.7924
128 | 34.7506 | 33.8042 | 33.7596 | 29.2719 | 27.3778 | 26.2035 | 24.9929 | 21.1461 | 18.7101 | 18.6564 | 21.6532 | 27.903 | 27.4692 | 24.6028 | 24.9526 | 25.3761 | 27.6121 | 26.3252 | 24.7558 | 27.0833 | 26.8913 | 25.9584 | 26.7551 | 28.7398
129 | 28.1448 | 26.8482 | 27.9096 | 29.002 | 27.4627 | 26.617 | 27.4602 | 26.6291 | 22.9919 | 22.8123 | 23.4679 | 22.3749 | 24.4197 | 26.1473 | 27.3016 | 30.0354 | 25.3148 | 32.6928 | 34.988 | 30.5699 | 30.4871 | 32.5988 | 35.7619 | 35.8783
130 | 37.9709 | 32.4141 | 29.2236 | 27.7328 | 26.8076 | 24.8054 | 24.0293 | 20.0798 | 16.981 | 17.7794 | 17.0868 | 18.8012 | 20.1325 | 21.8209 | 26.0364 | 28.5002 | 29.0461 | 32.2958 | 29.8256 | 28.6593 | 31.7332 | 33.7069 | 26.6974 | 28.0981
131 | 27.2849 | 23.8892 | 22.8635 | 24.151 | 25.1436 | 24.2956 | 23.9313 | 19.8128 | 17.226 | 17.5645 | 18.1321 | 20.5643 | 23.4041 | 23.537 | 24.7824 | 25.6251 | 26.8046 | 28.2525 | 25.979 | 30.6877 | 30.7438 | 29.249 | 28.841 | 28.7639
132 | 27.1835 | 24.5269 | 21.7813 | 19.9515 | 19.3533 | 16.9616 | 16.5419 | 15.1066 | 13.4231 | 14.4238 | 14.9285 | 16.6641 | 19.6704 | 20.0572 | 21.5516 | 22.8708 | 23.1128 | 24.8937 | 26.2948 | 26.7705 | 30.9707 | 29.0679 | 29.0136 | 27.6271
133 | 24.0902 | 21.0592 | 20.558 | 20.6557 | 20.6336 | 19.37 | 19.4285 | 17.5306 | 14.9729 | 16.6953 | 19.3529 | 20.313 | 20.4913 | 22.0089 | 25.2452 | 25.6257 | 27.2577 | 27.885 | 26.5897 | 27.3764 | 29.9264 | 29.798 | 26.7671 | 25.5347
134 | 22.1024 | 21.9433 | 22.552 | 25.0044 | 25.8347 | 23.8343 | 22.9194 | 19.6928 | 15.7272 | 14.3089 | 14.9385 | 16.4 | 18.4678 | 21.4255 | 20.5058 | 25.2545 | 26.9646 | 27.2827 | 27.4986 | 29.1111 | 31.7347 | 28.0042 | 26.8757 | 27.4701
135 | 22.5832 | 19.6748 | 23.4704 | 24.1736 | 24.1824 | 21.8466 | 23.2015 | 19.0521 | 14.8096 | 12.3435 | 14.9353 | 14.8286 | 18.872 | 19.4087 | 25.0056 | 24.9819 | 26.5334 | 27.7398 | 28.1918 | 29.1505 | 31.9428 | 32.227 | 33.6122 | 31.9349
136 | 28.7896 | 26.9965 | 27.7797 | 26.5898 | 26.5156 | 23.2564 | 20.8818 | 18.9441 | 17.559 | 17.5541 | 18.3159 | 18.7632 | 20.6386 | 20.8432 | 28.7888 | 29.741 | 31.0537 | 30.6948 | 35.0144 | 32.5499 | 30.9787 | 30.2538 | 26.4082 | 29.4406
137 | 27.3927 | 26.7054 | 26.7792 | 26.3163 | 25.9914 | 24.2475 | 22.7245 | 21.6379 | 19.8706 | 19.3673 | 19.3666 | 19.2736 | 19.6477 | 20.1238 | 23.0594 | 27.5841 | 24.0753 | 28.5597 | 26.5378 | 28.7365 | 27.6209 | 27.6766 | 28.3685 | 28.5945
138 | 29.2901 | 26.252 | 24.6474 | 24.3173 | 25.138 | 24.436 | 22.2193 | 17.3127 | 14.5082 | 13.1162 | 15.1735 | 15.8811 | 18.5661 | 19.4463 | 23.3413 | 23.9598 | 26.4552 | 30.5086 | 33.6868 | 33.2001 | 36.6485 | 35.6514 | 33.037 | 34.1916
139 | 30.2756 | 29.538 | 26.4828 | 26.6439 | 25.2897 | 19.874 | 20.3274 | 17.6186 | 13.6627 | 14.3291 | 16.4461 | 19.6546 | 19.5622 | 17.2356 | 19.157 | 23.4992 | 26.34 | 28.4062 | 27.1887 | 27.2258 | 28.622 | 24.9549 | 24.0808 | 26.0607
140 | 24.7497 | 21.648 | 21.866 | 23.4772 | 22.1427 | 20.3833 | 18.8502 | 16.5476 | 14.9351 | 12.5553 | 11.1151 | 12.066 | 16.0855 | 15.7659 | 20.1443 | 23.4417 | 24.4734 | 31.5622 | 29.9944 | 29.8928 | 31.8559 | 30.1143 | 30.8096 | 26.9534
141 | 24.9927 | 23.5481 | 22.6704 | 22.5426 | 23.7775 | 23.7099 | 23.5467 | 20.1442 | 17.5483 | 17.292 | 18.1277 | 20.9515 | 23.5452 | 23.8334 | 26.7626 | 27.6377 | 31.162 | 31.0888 | 33.8715 | 33.9701 | 36.0248 | 35.3274 | 34.4559 | 31.8347
142 | 29.9505 | 26.4984 | 25.0491 | 26.5467 | 25.4059 | 24.1523 | 22.7436 | 21.0592 | 20.3992 | 20.6461 | 17.8798 | 18.9604 | 20.6616 | 21.0584 | 22.5923 | 26.2512 | 33.4782 | 32.771 | 34.9975 | 32.1238 | 35.665 | 34.5004 | 35.7141 | 33.6121
143 | 30.1434 | 25.8488 | 23.7289 | 22.5947 | 20.7809 | 18.2809 | 15.9728 | 11.9294 | 10.3772 | 10.3235 | 11.8258 | 13.2971 | 16.2073 | 18.1096 | 20.1378 | 24.0611 | 27.4469 | 27.4383 | 28.9128 | 28.0448 | 31.0165 | 28.9444 | 25.853 | 26.6375
144 | 23.8282 | 21.0096 | 22.585 | 23.61 | 22.1188 | 19.5507 | 18.8009 | 18.7311 | 17.8328 | 17.4184 | 17.4805 | 17.0697 | 18.3022 | 19.4879 | 20.5256 | 25.3567 | 29.0654 | 32.1041 | 28.223 | 29.348 | 26.6719 | 26.1567 | 29.3725 | 26.7069
145 | 26.3571 | 20.4996 | 19.488 | 21.3439 | 20.2879 | 18.5604 | 16.514 | 13.2764 | 10.4625 | 9.5892 | 11.8278 | 16.0213 | 17.8971 | 19.8575 | 20.6596 | 24.0545 | 29.9478 | 27.8663 | 27.7764 | 27.6416 | 28.4242 | 25.5117 | 26.9346 | 24.5598
146 | 24.5856 | 20.68 | 19.2035 | 19.135 | 17.961 | 15.0998 | 12.8719 | 12.0809 | 11.7001 | 11.8567 | 14.4951 | 19.0421 | 21.571 | 21.549 | 24.6973 | 25.2478 | 25.1568 | 29.4264 | 29.5124 | 26.8921 | 30.0673 | 27.7766 | 25.1954 | 29.0925
147 | 28.564 | 28.0012 | 28.1869 | 26.7273 | 24.4226 | 21.864 | 18.2651 | 16.1355 | 11.9913 | 11.8476 | 13.0556 | 14.613 | 14.8111 | 14.4769 | 17.6182 | 23.2704 | 29.2348 | 31.8657 | 32.5251 | 33.2338 | 29.576 | 30.701 | 30.56 | 28.5984
148 | 26.6114 | 26.0252 | 25.4297 | 23.1177 | 22.1746 | 19.57 | 15.4893 | 12.2054 | 9.4563 | 8.8301 | 10.0222 | 13.2198 | 14.7691 | 16.6139 | 19.6123 | 22.232 | 25.5293 | 24.7307 | 28.6503 | 29.1229 | 27.2746 | 30.1564 | 30.2515 | 33.8714
149 | 31.0733 | 29.0363 | 27.9841 | 25.2523 | 23.2375 | 22.9246 | 20.0955 | 19.8658 | 16.3873 | 16.5683 | 17.9675 | 18.5972 | 23.6305 | 26.9675 | 31.2613 | 32.0142 | 32.9707 | 28.8238 | 36.1065 | 34.5258 | 34.4009 | 30.6782 | 30.4903 | 28.6543
150 | 25.8474 | 21.5172 | 21.2103 | 25.0609 | 22.6841 | 21.6723 | 19.7622 | 17.5941 | 15.1455 | 14.2014 | 13.1498 | 15.46 | 16.2962 | 20.2311 | 22.5611 | 26.9832 | 25.9564 | 28.7111 | 31.3905 | 28.2854 | 28.8538 | 30.1713 | 26.1207 | 28.4035
151 | 26.8506 | 24.5358 | 20.5414 | 18.4313 | 16.6341 | 15.3524 | 15.4102 | 12.4651 | 10.5519 | 9.9919 | 11.846 | 13.324 | 15.3208 | 17.5287 | 21.4331 | 25.5542 | 30.727 | 31.541 | 31.439 | 34.513 | 36.4721 | 33.5945 | 36.8674 | 33.3427
152 | 27.5286 | 24.0615 | 21.559 | 22.4013 | 24.6781 | 22.186 | 18.4136 | 17.847 | 16.8936 | 14.9741 | 15.372 | 17.582 | 18.0814 | 16.6986 | 21.4409 | 23.3342 | 29.1293 | 25.6663 | 31.0867 | 32.2239 | 34.3668 | 30.7673 | 27.4814 | 26.1822
153 | 26.5274 | 25.7333 | 23.7606 | 22.4681 | 20.1821 | 17.9631 | 13.0645 | 11.3899 | 11.0094 | 11.1812 | 11.1593 | 15.3476 | 19.5263 | 21.663 | 19.8371 | 25.8784 | 26.91 | 32.3093 | 39.1711 | 36.7052 | 37.8748 | 37.3453 | 34.99 | 33.0038
154 | 29.5098 | 26.8853 | 22.8944 | 20.5766 | 22.7092 | 20.6818 | 16.6328 | 13.7672 | 11.3704 | 11.6639 | 13.4853 | 12.9435 | 16.5678 | 16.4132 | 17.5244 | 22.041 | 21.5866 | 24.2826 | 30.2855 | 31.1342 | 28.6241 | 31.1629 | 26.1304 | 28.4092
155 | 28.465 | 23.3318 | 22.9741 | 22.4204 | 22.1253 | 20.5155 | 18.3867 | 15.7077 | 12.4823 | 11.8628 | 14.1191 | 18.5708 | 21.4641 | 20.2101 | 20.9879 | 29.8363 | 29.5892 | 31.7697 | 31.7971 | 28.1582 | 28.36 | 27.3306 | 28.7002 | 26.4818
156 | 25.2803 | 22.8748 | 23.0386 | 20.4593 | 22.845 | 20.234 | 19.2058 | 15.9618 | 14.7486 | 15.4489 | 15.7689 | 15.946 | 18.9702 | 17.1647 | 19.9091 | 27.4465 | 29.3566 | 28.9892 | 29.4646 | 32.7247 | 34.7418 | 33.3552 | 33.9047 | 29.4621
157 | 28.5741 | 27.4877 | 27.2115 | 26.6429 | 25.6731 | 23.1072 | 18.9455 | 18.3576 | 18.5112 | 19.119 | 20.2416 | 19.1545 | 19.7379 | 21.6101 | 24.9436 | 27.1701 | 29.7484 | 31.3076 | 32.8307 | 31.7206 | 30.5314 | 29.5705 | 37.0245 | 35.0544
158 | 33.8192 | 32.9168 | 29.8013 | 27.9947 | 27.4869 | 25.7972 | 23.5056 | 21.7194 | 22.0847 | 21.2552 | 20.6492 | 18.4322 | 19.9462 | 20.4196 | 22.3483 | 28.2078 | 29.1931 | 33.1347 | 30.805 | 34.5106 | 34.1404 | 35.749 | 34.4194 | 36.5917
159 | 31.9489 | 31.3179 | 30.3369 | 30.0239 | 27.166 | 25.4314 | 23.8977 | 20.422 | 16.048 | 13.4716 | 14.1052 | 18.7142 | 18.6804 | 19.3532 | 23.8938 | 28.4749 | 27.7399 | 25.7211 | 28.7783 | 33.2523 | 33.8698 | 32.4265 | 27.1432 | 31.6517
160 | 31.1995 | 30.2967 | 28.1069 | 24.5754 | 24.2792 | 24.579 | 22.1764 | 20.4008 | 19.5942 | 19.4679 | 18.7946 | 19.8815 | 23.4102 | 23.6663 | 21.1767 | 25.3994 | 26.4421 | 30.6893 | 34.0082 | 34.4973 | 34.6414 | 35.735 | 32.4757 | 33.9176
161 | 34.6388 | 29.3401 | 26.133 | 25.7396 | 24.5466 | 23.3949 | 19.1327 | 16.283 | 14.7713 | 15.4782 | 15.8736 | 17.7082 | 17.5466 | 15.3529 | 18.1577 | 27.5733 | 28.7001 | 38.3035 | 33.8242 | 30.0895 | 30.8731 | 29.388 | 29.8316 | 31.3661
162 | 34.433 | 32.0507 | 26.2377 | 24.6095 | 23.3682 | 23.1997 | 19.8096 | 19.0959 | 16.7431 | 15.95 | 15.1701 | 16.9812 | 21.6825 | 18.816 | 19.916 | 26.7368 | 31.9453 | 30.5198 | 32.444 | 30.394 | 32.7767 | 36.4469 | 35.4815 | 35.1715
163 | 29.8869 | 26.9031 | 25.143 | 25.0426 | 23.3419 | 22.5442 | 20.943 | 17.4758 | 16.3194 | 14.3858 | 15.4477 | 17.1978 | 19.4691 | 17.9286 | 18.6248 | 24.5101 | 30.6932 | 35.3793 | 32.3051 | 29.5747 | 32.6802 | 32.8487 | 32.4413 | 34.2164
164 | 29.8245 | 28.3009 | 25.2507 | 22.1821 | 24.0295 | 24.5223 | 20.2602 | 17.748 | 15.0689 | 13.3323 | 15.0991 | 16.0153 | 18.3625 | 18.7553 | 21.5844 | 27.5524 | 31.2455 | 29.5155 | 30.7872 | 30.5986 | 31.4547 | 30.5455 | 32.0393 | 30.4883
165 | 28.1523 | 29.4574 | 26.3075 | 25.2125 | 23.0141 | 21.3924 | 16.1203 | 13.1691 | 13.4894 | 14.8715 | 14.3135 | 16.4207 | 18.6723 | 21.1962 | 19.7278 | 25.0313 | 26.2318 | 33.3182 | 32.0769 | 32.5501 | 31.2842 | 31.882 | 30.8506 | 31.5751
166 | 30.2012 | 27.0383 | 27.6357 | 28.0835 | 24.5875 | 22.3512 | 16.9726 | 14.5817 | 13.4139 | 13.2044 | 12.4643 | 13.1112 | 13.6126 | 17.9222 | 16.717 | 24.1358 | 24.8369 | 30.9146 | 34.3916 | 33.1437 | 34.8604 | 29.3824 | 29.6511 | 30.0439
167 | 30.2309 | 29.6313 | 28.575 | 25.1634 | 23.8441 | 23.0421 | 21.7172 | 19.8687 | 19.4638 | 18.8796 | 17.0424 | 17.5214 | 20.0654 | 21.6958 | 24.3815 | 25.66 | 26.8717 | 33.4045 | 34.0309 | 34.9128 | 33.6949 | 29.9706 | 31.5944 | 33.4938
168 | 33.2686 | 30.776 | 30.6582 | 27.8075 | 25.3669 | 21.9882 | 16.9975 | 16.2575 | 14.6737 | 14.6659 | 14.3621 | 18.0308 | 17.8559 | 17.1606 | 23.0745 | 23.4838 | 25.5508 | 29.8486 | 32.7783 | 29.6376 | 30.187 | 31.6201 | 29.6342 | 31.7103
169 | 33.9935 | 30.7441 | 27.4652 | 24.9522 | 23.2152 | 23.0018 | 19.5732 | 17.8764 | 15.9743 | 16.1082 | 14.8295 | 15.9339 | 16.1963 | 15.6227 | 15.3774 | 21.9327 | 23.9103 | 26.4486 | 31.9961 | 30.8544 | 34.3727 | 36.498 | 32.3554 | 32.294
170 | 28.559 | 25.835 | 24.1044 | 22.1436 | 20.8536 | 20.9422 | 20.1114 | 16.6886 | 13.6289 | 13.1499 | 13.6232 | 14.6639 | 15.0444 | 13.5984 | 15.4974 | 21.7735 | 23.3372 | 25.9184 | 24.1327 | 29.4053 | 33.6768 | 34.6227 | 38.813 | 37.8031
171 | 35.2962 | 32.2499 | 32.5845 | 30.4912 | 26.4434 | 23.3246 | 19.3695 | 16.8751 | 16.8047 | 15.1447 | 13.9789 | 14.0802 | 15.0724 | 12.8742 | 18.4699 | 27.9526 | 26.2535 | 27.9775 | 30.0267 | 33.5021 | 29.5773 | 31.4592 | 30.9869 | 31.9097
172 | 32.1799 | 30.7997 | 28.3808 | 26.1602 | 24.8754 | 22.8689 | 21.7903 | 18.7591 | 17.9064 | 17.9003 | 17.7508 | 17.1301 | 18.518 | 16.3003 | 19.8899 | 23.0573 | 23.5286 | 30.689 | 30.7042 | 33.1642 | 36.619 | 32.6185 | 30.1267 | 30.1504
173 | 29.8355 | 25.636 | 24.5486 | 23.3905 | 23.0943 | 23.6294 | 21.665 | 20.0638 | 15.6641 | 13.9403 | 12.5466 | 12.8273 | 13.6285 | 13.4912 | 19.3911 | 22.451 | 26.4834 | 25.1514 | 27.0642 | 31.0852 | 29.5711 | 28.181 | 25.5743 | 29.2835
174 | 26.0865 | 24.2204 | 22.4059 | 23.6516 | 22.6664 | 19.4336 | 15.0764 | 13.7436 | 11.1353 | 10.8439 | 10.9251 | 12.8065 | 14.4078 | 13.1081 | 18.3409 | 22.5427 | 22.7811 | 27.7033 | 28.7088 | 29.4412 | 31.1645 | 28.0701 | 24.5393 | 23.4735
175 | 25.8875 | 21.4076 | 23.4681 | 20.2647 | 19.7052 | 20.4216 | 18.2132 | 15.5997 | 10.8815 | 12.4337 | 12.6476 | 12.6937 | 13.1766 | 13.2845 | 14.8851 | 23.1129 | 26.3668 | 35.7343 | 29.7891 | 30.0826 | 32.4865 | 31.0147 | 29.5823 | 28.1929
176 | 28.0639 | 25.3535 | 22.6411 | 21.974 | 21.1153 | 18.6218 | 15.7351 | 10.5272 | 8.3283 | 7.691 | 8.5962 | 11.6396 | 13.4331 | 15.1929 | 14.7679 | 22.9038 | 26.276 | 30.4837 | 30.0474 | 26.4378 | 28.9435 | 30.5457 | 30.315 | 29.6925
177 | 26.6358 | 26.8109 | 26.6448 | 24.0691 | 21.547 | 19.5636 | 17.7677 | 16.0403 | 15.1767 | 14.178 | 16.2874 | 20.5318 | 20.0347 | 19.935 | 16.934 | 25.6117 | 26.4578 | 31.2245 | 26.1237 | 23.3293 | 30.369 | 29.6173 | 29.4224 | 29.1956
178 | 25.2097 | 23.3615 | 23.0916 | 22.2715 | 21.44 | 19.2075 | 17.9862 | 14.7087 | 12.8205 | 13.5863 | 12.4124 | 14.9105 | 15.0602 | 13.8236 | 17.0977 | 17.5977 | 20.7055 | 22.7139 | 25.702 | 24.9221 | 27.68 | 28.0385 | 26.0055 | 23.2595
179 | 27.5467 | 25.4286 | 23.6203 | 21.2254 | 18.5824 | 16.8664 | 15.3708 | 13.7507 | 11.0254 | 8.8519 | 8.6252 | 10.0116 | 11.365 | 10.6461 | 15.2752 | 17.68 | 19.0596 | 26.7038 | 29.4663 | 25.8521 | 27.3216 | 27.4337 | 26.4936 | 28.5726
180 | 26.0673 | 23.722 | 20.7183 | 20.3142 | 20.2524 | 18.9206 | 16.7221 | 13.8747 | 12.8598 | 13.6638 | 12.8325 | 10.7351 | 13.7143 | 15.7297 | 15.928 | 17.9319 | 24.0692 | 28.9114 | 29.5576 | 24.8012 | 28.1126 | 24.5489 | 28.2149 | 28.1536
181 | 25.1921 | 23.5473 | 25.4935 | 19.9091 | 18.4081 | 17.6952 | 15.1795 | 13.4008 | 12.6594 | 13.9766 | 17.9263 | 16.1648 | 19.9527 | 19.1391 | 20.2991 | 25.5861 | 26.3049 | 25.4414 | 30.4971 | 28.879 | 34.8636 | 31.3175 | 27.1845 | 26.9815
182 | 26.0868 | 24.8573 | 26.3215 | 22.5742 | 18.5026 | 17.459 | 14.9792 | 13.3807 | 12.9253 | 12.7649 | 13.192 | 11.2594 | 12.6858 | 11.4711 | 17.7302 | 23.7851 | 24.031 | 25.5362 | 26.4915 | 32.8965 | 31.0316 | 32.8155 | 30.5467 | 31.0638
183 | 30.7031 | 31.0209 | 24.0333 | 21.8411 | 18.679 | 17.3885 | 16.5565 | 13.1916 | 11.9864 | 12.1005 | 11.1934 | 11.4779 | 13.0153 | 12.6704 | 17.1471 | 20.413 | 19.7107 | 24.817 | 27.4123 | 31.8429 | 35.8723 | 35.9169 | 31.4348 | 34.2107
184 | 30.0168 | 23.1172 | 23.5164 | 23.6005 | 24.5453 | 23.2624 | 19.079 | 17.0211 | 14.927 | 14.257 | 13.5828 | 11.7927 | 12.7849 | 11.0406 | 12.964 | 14.9719 | 20.7514 | 21.4201 | 28.2977 | 27.4587 | 30.628 | 26.8006 | 25.0611 | 29.1947
185 | 29.8469 | 29.5225 | 26.5376 | 26.2001 | 22.1577 | 22.0255 | 17.2916 | 13.8166 | 12.4806 | 13.5623 | 13.8596 | 14.2261 | 15.3879 | 14.2011 | 15.657 | 17.164 | 23.2982 | 26.8611 | 28.1826 | 24.6959 | 28.1638 | 34.6351 | 32.2487 | 31.4818
186 | 31.7214 | 31.0594 | 31.1765 | 28.6551 | 29.5112 | 24.3098 | 19.3618 | 16.9259 | 14.1583 | 14.4022 | 10.4063 | 9.1177 | 8.3616 | 7.351 | 14.161 | 16.8552 | 21.2895 | 23.1598 | 29.2831 | 27.8932 | 30.0794 | 24.0389 | 27.7975 | 29.1403
187 | 25.7085 | 24.4412 | 23.7061 | 21.8209 | 21.0847 | 21.7453 | 16.6469 | 14.0906 | 12.9164 | 12.0505 | 10.1861 | 9.7037 | 8.941 | 9.6999 | 11.823 | 18.6266 | 20.5157 | 21.7971 | 23.9849 | 28.6964 | 31.7654 | 32.3097 | 31.9968 | 34.738
188 | 32.958 | 28.022 | 24.2654 | 22.9983 | 22.8847 | 22.2913 | 22.9908 | 20.6074 | 16.85 | 15.2253 | 14.7107 | 13.279 | 11.9321 | 10.3527 | 12.5779 | 16.9244 | 21.8377 | 27.4615 | 25.8349 | 26.9039 | 28.252 | 28.7253 | 31.3189 | 27.3804
189 | 27.8502 | 23.3291 | 22.2694 | 21.3409 | 20.9892 | 18.9342 | 16.9611 | 14.1687 | 11.7087 | 14.4018 | 14.0417 | 12.9577 | 13.7532 | 13.3041 | 14.368 | 12.4243 | 19.3806 | 27.3682 | 25.2457 | 25.3611 | 27.8949 | 26.8974 | 25.0582 | 23.3544
190 | 24.6489 | 22.3259 | 20.0038 | 20.1179 | 15.7582 | 14.0968 | 12.4375 | 11.3719 | 8.0554 | 10.4587 | 11.2824 | 9.6259 | 8.2194 | 10.4135 | 10.0049 | 15.9249 | 19.1617 | 17.4632 | 24.5939 | 24.5955 | 27.8962 | 26.926 | 28.6542 | 27.0586
191 | 29.0622 | 25.4713 | 25.0865 | 22.7602 | 17.0825 | 17.7828 | 16.5755 | 15.6348 | 13.4096 | 12.2739 | 10.6464 | 9.6887 | 10.1762 | 10.6872 | 13.0699 | 13.4676 | 19.1053 | 28.5115 | 21.3431 | 23.3506 | 28.399 | 27.9709 | 29.0619 | 27.4786
192 | 28.6385 | 26.5444 | 26.4171 | 25.9333 | 22.3559 | 18.7191 | 17.968 | 12.9716 | 9.89 | 8.4946 | 5.4725 | 5.9621 | 7.5148 | 8.4686 | 7.9769 | 9.9191 | 16.0872 | 26.6741 | 27.0511 | 25.1749 | 25.0525 | 27.4275 | 26.3814 | 24.8589
193 | 25.2462 | 26.5656 | 25.0046 | 20.9202 | 16.9212 | 14.4409 | 12.3364 | 8.794 | 6.3168 | 7.6855 | 7.5307 | 7.4282 | 8.2625 | 8.0894 | 13.4406 | 19.5862 | 20.375 | 18.7244 | 23.0803 | 22.4143 | 24.6375 | 24.5541 | 24.5558 | 22.5396
194 | 25.1095 | 25.3807 | 23.4208 | 21.1815 | 16.1083 | 12.9184 | 11.2783 | 9.0986 | 6.8431 | 7.8495 | 7.6177 | 7.8666 | 10.2203 | 10.7563 | 11.394 | 9.4293 | 18.3762 | 23.9 | 22.3389 | 22.0653 | 26.6626 | 24.8684 | 23.8941 | 25.0228
195 | 25.0357 | 21.1536 | 22.3547 | 21.1848 | 16.5904 | 16.6518 | 13.6177 | 10.0053 | 9.6664 | 9.427 | 8.233 | 6.7233 | 7.9752 | 9.7822 | 10.4214 | 12.0709 | 11.9753 | 16.1451 | 15.8469 | 18.7074 | 23.1376 | 24.99 | 23.9944 | 25.3476
196 | 24.9358 | 24.1044 | 23.6464 | 19.4667 | 18.5202 | 18.6629 | 16.9598 | 13.3388 | 11.5986 | 11.7174 | 12.4817 | 12.5443 | 10.8338 | 10.9883 | 12.4062 | 13.083 | 19.0636 | 23.871 | 25.5216 | 22.0119 | 27.5015 | 27.69 | 25.7872 | 26.9822
197 | 30.1222 | 28.6193 | 26.6198 | 24.1148 | 19.8592 | 19.5711 | 19.2021 | 12.9137 | 9.211 | 8.9261 | 11.0466 | 11.4744 | 12.548 | 11.6537 | 14.0686 | 16.0911 | 14.3925 | 20.3832 | 22.3842 | 22.88 | 27.9772 | 30.2386 | 26.8083 | 26.513
198 | 30.283 | 28.91 | 27.7435 | 27.4448 | 22.7873 | 20.0267 | 16.7501 | 12.3856 | 10.8839 | 12.4215 | 13.7519 | 11.5068 | 11.0191 | 11.1279 | 9.1105 | 13.4435 | 17.5477 | 20.8663 | 22.1417 | 20.1729 | 24.9203 | 27.8052 | 29.2068 | 28.9947
199 | 31.2489 | 28.3716 | 25.8182 | 22.3852 | 20.6779 | 18.9044 | 16.1884 | 12.9544 | 10.2082 | 7.9262 | 8.444 | 7.7299 | 7.496 | 7.1649 | 11.6336 | 13.56 | 18.4436 | 21.2994 | 24.2188 | 29.2948 | 27.9112 | 31.5608 | 28.9133 | 31.2331
200 | 33.4338 | 29.1706 | 28.5093 | 24.6311 | 21.072 | 18.7014 | 17.7076 | 12.3483 | 9.8668 | 11.1793 | 11.1505 | 8.665 | 8.4103 | 8.6543 | 10.5943 | 15.708 | 15.314 | 20.0833 | 22.566 | 24.4193 | 25.9578 | 25.3725 | 27.2183 | 26.1838
201 | 27.3335 | 28.745 | 28.4465 | 23.3541 | 18.0704 | 14.6863 | 12.5306 | 9.2305 | 5.6647 | 5.3224 | 5.1176 | 7.2374 | 9.7883 | 8.5279 | 8.9572 | 15.6021 | 17.1019 | 25.9012 | 29.18 | 26.89 | 27.5922 | 24.1111 | 20.7662 | 23.0872
202 | 23.5172 | 21.93 | 19.0174 | 15.7545 | 14.4283 | 14.4762 | 16.2715 | 14.0592 | 10.5115 | 10.7645 | 9.4208 | 8.1096 | 7.758 | 8.7105 | 10.6809 | 11.7327 | 17.1633 | 22.1698 | 23.7722 | 27.2043 | 29.3327 | 31.9872 | 28.1309 | 26.817
203 | 27.0344 | 26.0607 | 26.1865 | 22.1022 | 17.7594 | 14.7641 | 14.5847 | 10.7662 | 8.2074 | 7.7269 | 7.7679 | 6.6259 | 6.9228 | 6.5455 | 11.5869 | 10.922 | 18.1188 | 23.485 | 20.8833 | 22.0958 | 27.2722 | 26.7772 | 26.576 | 29.688
204 | 25.5083 | 22.1192 | 22.6871 | 21.5972 | 20.8639 | 18.6584 | 17.8234 | 14.759 | 11.2134 | 9.5575 | 9.5116 | 9.8789 | 10.8028 | 12.2455 | 12.9042 | 16.7258 | 19.443 | 27.9386 | 22.7125 | 21.8315 | 23.8402 | 29.0536 | 22.4307 | 25.7884
205 | 24.7496 | 22.9244 | 23.1931 | 21.5106 | 15.463 | 15.516 | 15.0454 | 11.6452 | 10.2781 | 10.6494 | 10.6626 | 10.5483 | 10.1043 | 10.7783 | 10.1134 | 13.7398 | 14.4261 | 21.8836 | 22.3755 | 22.0119 | 21.6887 | 28.4544 | 24.5348 | 26.8914
206 | 23.8753 | 20.5905 | 19.7047 | 18.2311 | 16.2572 | 17.6194 | 17.6521 | 13.7553 | 11.539 | 11.4082 | 10.112 | 10.9023 | 11.2918 | 10.9998 | 11.335 | 13.3112 | 15.4338 | 20.6573 | 21.551 | 22.4711 | 26.1765 | 27.6662 | 23.3601 | 26.4013
207 | 23.9013 | 21.63 | 20.6441 | 19.2507 | 16.3436 | 16.8586 | 14.6856 | 12.7026 | 11.5065 | 11.9513 | 11.3392 | 10.3591 | 11.4141 | 10.6445 | 11.9692 | 13.8364 | 18.4399 | 28.0714 | 22.5934 | 21.4879 | 24.2358 | 28.1569 | 25.6101 | 26.0113
208 | 23.9519 | 25.8839 | 25.2689 | 23.1066 | 20.0093 | 17.5554 | 14.602 | 10.9705 | 8.4561 | 8.6722 | 8.7199 | 8.139 | 9.29 | 8.0023 | 11.0624 | 11.2666 | 13.7723 | 19.1842 | 19.8515 | 18.5346 | 26.7507 | 26.4286 | 20.9883 | 21.7889
209 | 22.5303 | 18.7178 | 19.9623 | 15.9457 | 15.3082 | 14.9207 | 14.1131 | 10.7421 | 10.4112 | 11.2631 | 7.2842 | 6.7695 | 7.8611 | 7.6121 | 8.2683 | 16.981 | 23.4098 | 22.8796 | 22.5064 | 21.6892 | 28.8348 | 24.1695 | 25.2086 | 22.6421
210 | 21.2661 | 20.975 | 18.8749 | 17.655 | 16.1053 | 13.897 | 14.4724 | 12.5725 | 11.3696 | 11.8495 | 11.3696 | 7.6075 | 7.2552 | 9.7625 | 13.3484 | 15.2986 | 15.2838 | 18.889 | 22.8714 | 21.0397 | 27.6468 | 24.6831 | 26.1788 | 25.8482
211 | 26.6618 | 23.9059 | 23.2798 | 25.9581 | 23.0678 | 19.9129 | 19.6973 | 13.7784 | 11.7891 | 10.1774 | 8.0543 | 6.631 | 5.6804 | 6.1968 | 7.6696 | 10.7346 | 19.8 | 20.0345 | 26.698 | 24.9128 | 27.1145 | 27.4624 | 25.588 | 24.4443
212 | 25.0152 | 23.6565 | 20.8771 | 19.3792 | 17.5201 | 16.5008 | 15.8482 | 13.2522 | 10.0292 | 9.6872 | 11.6032 | 9.9257 | 8.5736 | 11.4086 | 10.3092 | 12.4359 | 14.7736 | 19.2185 | 23.9694 | 23.0847 | 29.2733 | 25.5043 | 19.8788 | 22.0319
213 | 26.2619 | 23.6176 | 23.158 | 22.4847 | 21.6915 | 22.1934 | 22.832 | 17.9324 | 13.574 | 12.7357 | 12.7798 | 11.6897 | 11.1129 | 12.1601 | 12.5272 | 17.8215 | 17.2692 | 22.6646 | 26.9637 | 26.492 | 26.3611 | 23.1332 | 23.7482 | 22.7612
214 | 22.613 | 23.7809 | 22.4808 | 19.3793 | 19.8775 | 18.34 | 16.0525 | 14.092 | 10.653 | 10.7208 | 10.1246 | 8.68 | 9.6662 | 9.3646 | 9.3635 | 10.3694 | 16.7265 | 20.9145 | 17.9947 | 24.2286 | 23.8398 | 25.5697 | 25.0524 | 26.4685
215 | 23.4303 | 25.4202 | 23.6495 | 22.7285 | 21.1516 | 18.8245 | 20.3058 | 17.101 | 11.7856 | 10.9491 | 10.0049 | 9.3784 | 10.6731 | 10.2578 | 12.038 | 14.3506 | 14.773 | 23.6157 | 27.82 | 23.4039 | 29.8788 | 25.921 | 30.5961 | 27.4782
216 | 26.8046 | 23.4085 | 20.2355 | 18.7119 | 18.352 | 18.104 | 15.8832 | 12.1057 | 8.5509 | 8.8342 | 8.4515 | 7.289 | 6.9599 | 6.2207 | 14.6781 | 18.0633 | 16.1353 | 19.3004 | 25.5589 | 27.5042 | 27.0329 | 25.7347 | 22.1113 | 25.4924
217 | 24.4335 | 20.5123 | 21.7869 | 21.8759 | 19.4968 | 17.1717 | 15.3984 | 11.1154 | 7.6224 | 6 | 4.1907 | 5.3585 | 8.045 | 7.3781 | 13.3891 | 14.8461 | 17.6006 | 22.4684 | 26.2517 | 23.3811 | 22.9109 | 24.0209 | 24.8468 | 27.8214
218 | 29.7622 | 26.1304 | 23.4076 | 22.899 | 22.3992 | 19.1053 | 19.2826 | 16.92 | 14.9015 | 13.1222 | 11.0325 | 11.1619 | 9.3726 | 8.1551 | 8.5296 | 14.1049 | 17.2676 | 17.4664 | 19.6358 | 25.0893 | 23.6091 | 25.6436 | 31.4655 | 25.456
219 | 25.6344 | 24.6472 | 22.5381 | 21.1338 | 22.6155 | 18.9984 | 16.4311 | 13.7419 | 10.7612 | 9.7797 | 9.3556 | 7.8654 | 8.2149 | 10.4013 | 13.6509 | 15.7769 | 19.5826 | 24.7979 | 23.9702 | 25.6588 | 23.9787 | 22.1543 | 22.2933 | 24.8628
220 | 22.8016 | 20.7914 | 21.3125 | 22.4931 | 21.2573 | 18.2291 | 18.3126 | 15.622 | 12.332 | 11.2195 | 10.6399 | 9.1037 | 7.5842 | 8.9454 | 12.4553 | 14.0208 | 16.6217 | 20.3921 | 23.4986 | 24.9046 | 25.2688 | 19.2084 | 22.314 | 21.7529
221 | 23.6792 | 22.3382 | 20.6325 | 20.6527 | 18.733 | 15.7138 | 15.3933 | 12.84 | 8.9119 | 9.1452 | 8.596 | 6.6337 | 6.8718 | 9.7678 | 8.4728 | 12.519 | 15.4888 | 20.5204 | 25.9129 | 25.2694 | 24.0777 | 24.9821 | 21.4709 | 22.8676
222 | 19.3592 | 18.0736 | 16.7966 | 14.0685 | 13.8675 | 11.3251 | 11.325 | 8.1953 | 6.6814 | 5.5633 | 5.8056 | 6.8947 | 7.2572 | 9.9963 | 15.5689 | 15.6268 | 18.0507 | 20.9915 | 25.5993 | 25.1612 | 22.9744 | 27.9333 | 22.0414 | 23.2731
223 | 20.8327 | 19.2107 | 17.6469 | 17.5015 | 16.9829 | 14.3897 | 12.2671 | 10.8387 | 9.3189 | 8.2563 | 8.2119 | 8.9877 | 8.0363 | 8.8991 | 12.865 | 14.1974 | 15.4802 | 24.172 | 23.3755 | 25.7772 | 30.1084 | 25.1919 | 24.9537 | 24.494
224 | 22.4849 | 21.7608 | 22.5822 | 22.2357 | 22.3618 | 21.528 | 22.4527 | 18.1663 | 12.0321 | 8.4663 | 7.3335 | 7.8207 | 7.3901 | 8.9402 | 11.6047 | 11.7549 | 14.9616 | 19.097 | 21.2685 | 25.4196 | 27.9127 | 24.6458 | 23.6566 | 22.0373
225 | 21.6992 | 20.9435 | 21.7866 | 19.4919 | 20.2442 | 18.0406 | 14.5186 | 11.6406 | 7.6577 | 7.173 | 7.3133 | 7.1116 | 8.1275 | 9.5507 | 12.9885 | 12.6778 | 20.1493 | 22.4293 | 26.3096 | 20.2245 | 28.5702 | 28.386 | 30.3353 | 28.6859
226 | 26.6334 | 26.7936 | 23.617 | 24.6545 | 21.2724 | 20.2307 | 19.9317 | 16.3459 | 12.0465 | 12.155 | 11.9196 | 10.958 | 9.3341 | 7.4514 | 8.5935 | 14.2879 | 13.8657 | 19.0173 | 21.4172 | 25.3089 | 24.5208 | 25.2138 | 25.2096 | 29.5953
227 | 30.3686 | 28.2721 | 26.749 | 28.0619 | 26.6408 | 24.9149 | 22.0162 | 18.9705 | 16.0049 | 17.3723 | 14.5853 | 11.9757 | 11.3852 | 11.4576 | 13.2464 | 14.2093 | 14.2253 | 23.791 | 24.7997 | 20.0049 | 27.7954 | 33.9685 | 31.0198 | 30.316
228 | 30.4086 | 27.2573 | 25.0199 | 25.2682 | 23.4306 | 22.137 | 21.489 | 16.5331 | 14.3519 | 14.5379 | 12.1985 | 10.2158 | 9.3448 | 12.111 | 10.4839 | 15.3441 | 17.5999 | 20.5699 | 22.4463 | 20.7802 | 21.9434 | 23.4254 | 22.8996 | 27.3208
229 | 25.1907 | 25.3689 | 24.1078 | 21.6104 | 20.854 | 17.3628 | 14.0238 | 11.3059 | 6.4702 | 4.8778 | 3.3559 | 3.8294 | 5.2149 | 10.2359 | 11.0495 | 17.237 | 18.9673 | 24.8448 | 25.3942 | 26.1336 | 27.2653 | 27.1731 | 26.1724 | 28.3962
230 | 28.4395 | 27.3484 | 22.4635 | 20.8489 | 26.2622 | 24.1789 | 22.6614 | 22.8835 | 15.7286 | 13.3806 | 11.8008 | 9.9013 | 10.1518 | 11.6805 | 11.4747 | 13.8814 | 19.8175 | 20.2036 | 18.772 | 25.0188 | 26.0074 | 25.4869 | 23.806 | 24.0213
231 | 24.7733 | 24.566 | 23.3627 | 23.155 | 21.2014 | 17.1667 | 14.6351 | 13.0846 | 9.5782 | 8.2243 | 9.5773 | 10.0723 | 10.0838 | 10.8649 | 13.0911 | 14.0997 | 19.4665 | 21.7378 | 27.3114 | 20.9102 | 21.6682 | 21.9755 | 22.4747 | 21.233
232 | 24.9546 | 23.2964 | 18.9402 | 21.1851 | 20.7097 | 18.2334 | 17.4882 | 17.2044 | 14.3574 | 13.1857 | 12.7214 | 12.2176 | 9.8998 | 12.074 | 10.63 | 10.5419 | 9.3242 | 11.5262 | 16.3956 | 21.6266 | 21.0975 | 23.9757 | 24.6421 | 27.0816
233 | 26.6676 | 27.2081 | 24.3108 | 22.0006 | 22.3174 | 22.6256 | 21.3868 | 18.6365 | 14.2153 | 13.1797 | 9.2024 | 7.6169 | 7.2536 | 6.5856 | 9.6597 | 9.8477 | 12.2041 | 15.7031 | 24.8645 | 25.6778 | 30.5677 | 27.9156 | 31.6238 | 31.7623
234 | 28.7131 | 27.2285 | 25.8703 | 25.0679 | 24.6641 | 24.2515 | 23.3985 | 21.1737 | 14.9708 | 13.4245 | 10.1145 | 8.9299 | 7.6763 | 8.2123 | 12.6095 | 14.6195 | 17.2247 | 22.0556 | 25.3233 | 19.3538 | 23.94 | 22.7675 | 26.3723 | 30.5901
235 | 32.5698 | 27.423 | 26.4453 | 26.2051 | 22.8907 | 21.0215 | 21.7223 | 17.8615 | 13.8879 | 12.5689 | 13.1201 | 11.9121 | 10.7028 | 12.2881 | 15.3504 | 16.2566 | 17.1637 | 22.1407 | 22.734 | 27.8413 | 26.7602 | 27.8481 | 29.199 | 31.552
236 | 32.1706 | 27.8822 | 28.5557 | 29.2706 | 28.1944 | 24.0011 | 25.6685 | 23.3203 | 17.4704 | 15.4909 | 14.0112 | 13.2179 | 10.3462 | 10.5349 | 15.5909 | 16.9576 | 17.3714 | 21.8959 | 25.6926 | 28.5389 | 29.3273 | 28.8524 | 27.3642 | 28.6034
237 | 26.4604 | 26.7456 | 24.2256 | 23.2705 | 22.2349 | 22.5335 | 21.1881 | 20.3259 | 15.7071 | 12.9454 | 12.4725 | 10.4566 | 9.487 | 9.1928 | 14.911 | 15.9995 | 18.0556 | 23.9677 | 20.7954 | 27.1404 | 25.5262 | 24.6941 | 25.439 | 26.4809
238 | 25.8571 | 22.39 | 21.992 | 24.6495 | 22.3515 | 19.7936 | 19.4 | 17.0611 | 12.3471 | 11.1924 | 9.8706 | 8.2644 | 6.9675 | 8.6858 | 12.6396 | 15.0705 | 16.9193 | 20.2329 | 23.0753 | 23.9049 | 23.162 | 24.942 | 29.5925 | 30.521
239 | 24.8235 | 21.8169 | 20.8402 | 18.6354 | 17.5505 | 15.9666 | 15.9617 | 13.9633 | 13.2964 | 13.3612 | 12.4054 | 10.2613 | 9.6084 | 9.6798 | 14.6049 | 12.1658 | 17.1872 | 19.7268 | 21.6679 | 20.7848 | 25.1858 | 26.3648 | 25.8679 | 28.0632
240 | 26.3992 | 24.3355 | 22.8289 | 20.8178 | 19.9388 | 19.3887 | 17.4604 | 14.8443 | 9.1873 | 7.2278 | 6.5489 | 7.2231 | 7.8335 | 10.0778 | 12.8651 | 12.5004 | 15.0389 | 19.0475 | 20.1431 | 21.8671 | 24.0481 | 25.8368 | 26.431 | 23.5005
241 | 23.5281 | 22.7669 | 23.6008 | 22.5868 | 20.6991 | 19.7303 | 17.8252 | 14.311 | 11.2664 | 9.5099 | 9.3194 | 7.4706 | 9.0243 | 9.8713 | 12.1341 | 13.223 | 14.5636 | 19.2486 | 23.4097 | 22.7131 | 25.8408 | 29.111 | 29.7174 | 29.8352
242 | 29.0143 | 26.2835 | 23.9222 | 24.5008 | 24.0312 | 23.6037 | 20.879 | 19.9588 | 15.3353 | 14.4129 | 11.8929 | 11.566 | 11.316 | 10.3448 | 13.1019 | 13.7334 | 19.2009 | 25.5752 | 26.5303 | 28.9472 | 30.3327 | 32.7625 | 31.309 | 30.0081
243 | 30.469 | 31.5123 | 29.2475 | 26.8251 | 26.2699 | 25.8071 | 21.9622 | 19.0047 | 13.6546 | 12.961 | 12.7995 | 11.8127 | 13.0542 | 14.207 | 15.301 | 14.1672 | 16.2239 | 18.5168 | 23.629 | 27.2698 | 28.2087 | 28.4061 | 25.9996 | 26.2312
244 | 26.4015 | 22.9447 | 19.654 | 18.949 | 19.5969 | 18.6548 | 17.756 | 14.8812 | 10.4458 | 10.6648 | 9.8568 | 9.0057 | 10.473 | 14.8351 | 17.6613 | 16.7784 | 16.0457 | 16.0433 | 20.3608 | 28.6845 | 30.781 | 31.4594 | 23.5041 | 24.6699
245 | 26.2665 | 21.2541 | 19.4563 | 19.0504 | 18.3606 | 18.5866 | 18.4219 | 16.0956 | 12.0319 | 13.4263 | 12.5129 | 10.3258 | 9.1034 | 8.9781 | 12.5376 | 11.4103 | 14.1226 | 17.7927 | 18.3375 | 23.6884 | 25.9226 | 28.7395 | 26.7969 | 26.3035
246 | 31.1218 | 27.3095 | 26.7866 | 24.3599 | 23.181 | 21.3255 | 21.1965 | 19.8566 | 15.7889 | 12.841 | 13.1898 | 12.1005 | 10.0731 | 12.166 | 13.2091 | 13.9581 | 17.2192 | 20.9514 | 24.7551 | 27.2663 | 29.864 | 32.6878 | 30.975 | 27.6312
247 | 27.9546 | 26.6845 | 24.6259 | 22.5039 | 21.9734 | 21.0895 | 18.6442 | 15.9298 | 11.4539 | 8.3372 | 6.8273 | 7.3513 | 7.4334 | 9.7887 | 16.6794 | 18.0035 | 19.6616 | 20.9711 | 23.8135 | 29.6599 | 28.338 | 32.3763 | 34.1252 | 31.1434
248 | 31.5024 | 25.0639 | 24.2469 | 27.3075 | 25.859 | 25.595 | 25.3298 | 22.459 | 17.2991 | 15.7389 | 14.4288 | 13.7027 | 11.9155 | 10.8149 | 10.1736 | 11.7066 | 12.9269 | 21.359 | 25.7413 | 30.2403 | 31.2495 | 28.5191 | 30.1055 | 28.0301
249 | 29.0486 | 28.0591 | 28.2708 | 27.9507 | 25.4254 | 24.3357 | 23.7101 | 21.6977 | 17.323 | 14.9488 | 12.2392 | 10.938 | 9.5235 | 11.7256 | 15.9758 | 19.0234 | 19.8849 | 22.082 | 28.3251 | 30.5539 | 27.805 | 29.9067 | 30.5506 | 32.7034
250 | 29.5138 | 27.3949 | 24.9062 | 24.448 | 23.4274 | 21.9349 | 20.0782 | 19.6554 | 15.4806 | 15.5878 | 13.9649 | 13.3116 | 13.2161 | 14.0631 | 15.5171 | 15.1796 | 18.8068 | 21.9093 | 21.6755 | 25.3396 | 30.0427 | 28.3908 | 27.9811 | 27.3301
251 | 27.5671 | 23.9416 | 22.8823 | 21.9682 | 20.3895 | 19.9762 | 19.3256 | 17.9573 | 13.6575 | 13.1929 | 13.6425 | 12.8814 | 11.6466 | 11.4004 | 13.5407 | 16.8407 | 16.4593 | 16.6832 | 23.1641 | 26.6907 | 28.4823 | 29.8039 | 31.6303 | 32.0009
252 | 29.0994 | 25.9099 | 25.4719 | 22.5028 | 22.7145 | 19.5329 | 20.1779 | 17.1848 | 13.3884 | 13.7693 | 13.926 | 14.1956 | 14.0975 | 14.837 | 15.615 | 17.4894 | 21.9607 | 22.6856 | 26.2893 | 28.3617 | 29.6512 | 31.5828 | 30.4249 | 27.9333
253 | 26.6193 | 25.8045 | 23.1692 | 24.1412 | 23.9791 | 26.9885 | 26.5811 | 23.9087 | 19.5406 | 18.8596 | 18.7589 | 18.6985 | 19.6268 | 19.9335 | 18.2724 | 17.5324 | 19.8788 | 21.3294 | 22.3766 | 29.0326 | 33.1849 | 31.5074 | 28.4115 | 28.3386
254 | 27.0283 | 25.3047 | 25.8306 | 24.5028 | 23.5529 | 21.4505 | 20.6088 | 18.7792 | 15.5375 | 16.2515 | 16.6371 | 16.8098 | 18.4559 | 17.1811 | 19.825 | 19.9029 | 16.6101 | 20.1208 | 24.3747 | 29.1571 | 28.8042 | 31.4174 | 32.1731 | 31.6476
255 | 29.4877 | 25.9873 | 24.6349 | 25.6882 | 24.5228 | 24.572 | 22.1847 | 21.5184 | 17.671 | 16.8799 | 16.0432 | 15.1984 | 14.3195 | 14.8538 | 15.2575 | 14.216 | 17.1755 | 21.507 | 20.2007 | 20.0575 | 20.0138 | 24.0243 | 26.326 | 26.5013
256 | 26.5213 | 22.4427 | 23.0801 | 20.8215 | 18.9646 | 18.9365 | 18.4195 | 17.1532 | 12.734 | 10.4436 | 11.4533 | 11.4543 | 11.5265 | 15.4305 | 14.8434 | 16.733 | 20.7241 | 21.0924 | 24.3501 | 26.0269 | 24.1359 | 25.2896 | 27.6487 | 26.0607
257 | 25.142 | 19.6912 | 18.7419 | 19.3932 | 20.7116 | 19.8272 | 17.8078 | 16.7706 | 14.2105 | 13.3899 | 13.5968 | 14.9889 | 15.6225 | 18.0104 | 16.7027 | 17.8131 | 20.4534 | 26.1857 | 26.4126 | 33.605 | 34.1992 | 35.3902 | 33.4099 | 30.5776
258 | 32.6294 | 27.2995 | 23.5886 | 21.5493 | 23.7855 | 23.3345 | 22.7404 | 22.5995 | 19.5557 | 18.7143 | 17.9716 | 17.2584 | 16.7299 | 17.3951 | 19.1917 | 17.4058 | 20.3667 | 24.4493 | 27.3541 | 28.6021 | 28.9618 | 28.2023 | 30.2167 | 29.4007
259 | 27.0602 | 25.0596 | 23.0534 | 21.6777 | 22.3871 | 21.7712 | 19.4151 | 17.4614 | 14.8621 | 13.8398 | 13.2274 | 13.4933 | 15.36 | 17.9209 | 19.0947 | 15.4043 | 16.8885 | 20.7907 | 29.0748 | 29.0133 | 27.1165 | 27.5651 | 27.2023 | 25.9751
260 | 28.4723 | 24.3992 | 25.8618 | 28.1128 | 26.3055 | 24.9134 | 24.8203 | 24.4889 | 22.0091 | 20.7978 | 19.4084 | 17.8285 | 17.7203 | 19.5937 | 18.4749 | 19.6843 | 17.1713 | 20.6009 | 21.6216 | 24.7429 | 24.1648 | 32.0741 | 30.8572 | 33.1392
261 | 30.9679 | 26.0696 | 24.8833 | 25.0049 | 24.4069 | 23.1356 | 21.0172 | 18.5571 | 13.6182 | 10.8015 | 10.8558 | 12.6513 | 15.1658 | 18.4863 | 18.4476 | 17.7089 | 22.0272 | 26.6313 | 31.5705 | 33.6681 | 29.0759 | 28.1622 | 30.2686 | 30.1535
262 | 30.0649 | 29.3352 | 27.8152 | 24.0486 | 23.2767 | 21.6252 | 21.9215 | 20.6682 | 16.9883 | 13.2254 | 12.9981 | 13.7046 | 12.8252 | 13.0756 | 13.0189 | 14.2652 | 16.0742 | 19.0382 | 21.1716 | 23.1716 | 24.3717 | 32.4972 | 30.443 | 28.2369
263 | 29.5578 | 25.4547 | 24.3514 | 23.0059 | 24.6615 | 23.6983 | 22.3719 | 21.5434 | 17.0874 | 16.9302 | 17.1132 | 17.7698 | 15.7981 | 16.2966 | 16.1587 | 16.1863 | 19.7143 | 23.7669 | 25.9279 | 28.4319 | 29.3461 | 29.8009 | 26.1926 | 24.3739
264 | 24.4323 | 22.041 | 21.746 | 22.0554 | 24.2714 | 24.4389 | 22.3863 | 21.4831 | 18.5799 | 19.4087 | 19.7766 | 19.7623 | 20.762 | 20.9989 | 20.8909 | 22.4271 | 23.6309 | 26.9618 | 29.7872 | 30.9608 | 29.2911 | 30.8386 | 31.1318 | 31.6211
265 | 28.9193 | 28.4331 | 27.075 | 24.4623 | 23.2844 | 21.6663 | 18.5641 | 16.3522 | 13.6743 | 11.9388 | 13.6619 | 15.2785 | 15.9171 | 16.5283 | 20.1568 | 19.339 | 23.8691 | 26.5981 | 31.0332 | 30.3635 | 26.7339 | 23.9331 | 21.4145 | 22.4534
266 | 22.4111 | 20.6032 | 20.4121 | 22.3277 | 24.1178 | 24.7178 | 26.5937 | 24.8517 | 21.3979 | 19.9707 | 19.8868 | 20.0727 | 18.5089 | 20.2838 | 21.4327 | 20.6436 | 22.7988 | 25.8725 | 26.1479 | 25.3149 | 25.1046 | 24.346 | 21.0527 | 23.0017
267 | 21.7186 | 19.1383 | 20.1112 | 18.2187 | 16.111 | 13.5755 | 12.5735 | 14.6194 | 11.9555 | 10.4847 | 9.8465 | 12.4927 | 12.6514 | 11.5949 | 12.1784 | 12.7696 | 13.7221 | 16.6936 | 20.9617 | 24.6288 | 23.0632 | 25.2175 | 22.2064 | 25.1886
268 | 21.3961 | 19.881 | 20.855 | 19.1801 | 20.6446 | 19.6015 | 19.0228 | 18.1044 | 14.8176 | 11.9822 | 12.9088 | 11.9224 | 10.9914 | 11.5508 | 15.4669 | 16.7502 | 19.2181 | 21.161 | 25.1184 | 25.6391 | 25.1779 | 25.7785 | 25.5479 | 28.8085
269 | 25.9752 | 21.5826 | 18.6296 | 18.9527 | 17.8105 | 17.5789 | 14.3919 | 13.2529 | 12.3323 | 10.0369 | 11.0317 | 12.7337 | 10.4778 | 10.7377 | 12.871 | 11.571 | 15.4509 | 19.4989 | 26.175 | 28.8473 | 31.2659 | 27.9842 | 27.3689 | 27.6368
270 | 25.2832 | 22.0507 | 19.6287 | 19.4584 | 18.4741 | 20.7471 | 20.9868 | 19.3439 | 14.6506 | 11.5122 | 11.7209 | 10.9483 | 12.2325 | 13.7901 | 15.4813 | 15.3613 | 18.1199 | 20.7123 | 28.7859 | 31.5447 | 28.5141 | 27.3033 | 25.86 | 22.7959
271 | 22.0148 | 21.615 | 19.5954 | 17.9829 | 18.065 | 16.5517 | 16.0525 | 14.3322 | 12.9425 | 10.9804 | 12.6362 | 13.7128 | 16.3025 | 16.1378 | 16.7281 | 18.5318 | 19.756 | 17.8148 | 21.9683 | 24.6426 | 24.3001 | 24.0447 | 22.4999 | 21.9627
272 | 23.9685 | 21.1578 | 20.0428 | 20.0227 | 23.1292 | 25.094 | 24.5567 | 21.9413 | 19.1475 | 17.7318 | 17.4409 | 16.1791 | 15.9497 | 16.2785 | 17.3441 | 19.3023 | 19.6545 | 20.8579 | 28.3034 | 29.019 | 29.1968 | 27.5455 | 25.6701 | 24.9215
273 | 24.3169 | 21.6312 | 23.2689 | 24.1867 | 22.5606 | 22.803 | 21.4351 | 22.6497 | 19.7906 | 18.6767 | 17.13 | 15.2054 | 15.4086 | 15.5546 | 14.4305 | 15.1887 | 18.9731 | 20.6487 | 26.3813 | 27.4884 | 26.3465 | 25.1634 | 26.0328 | 26.8989
274 | 26.3173 | 23.8705 | 24.8732 | 23.3885 | 22.9265 | 22.6813 | 22.5987 | 22.3966 | 19.3771 | 17.7088 | 16.7922 | 16.2678 | 15.4584 | 16.2286 | 16.8324 | 17.8471 | 18.535 | 22.9175 | 21.1924 | 24.6146 | 28.491 | 28.6627 | 27.0047 | 26.6835
275 | 25.5078 | 23.7296 | 25.9569 | 25.9553 | 25.7601 | 26.3688 | 27.3324 | 24.6088 | 20.9353 | 18.9809 | 18.2827 | 15.8808 | 14.1714 | 15.7049 | 15.7299 | 14.557 | 17.7999 | 22.6577 | 22.8604 | 23.1021 | 24.9351 | 24.7395 | 26.6693 | 27.9928
276 | 27.1616 | 26.1331 | 22.9418 | 22.8001 | 23.6956 | 24.0766 | 23.2932 | 20.3657 | 16.6048 | 12.5209 | 13.4476 | 14.4787 | 16.4424 | 18.5303 | 22.6013 | 23.6592 | 26.8851 | 27.7387 | 32.6356 | 31.6461 | 30.3743 | 30.3914 | 29.3312 | 26.9051
277 | 24.8709 | 24.1638 | 24.8547 | 23.2302 | 23.6026 | 24.3182 | 22.4493 | 21.8526 | 18.8164 | 18.1829 | 16.5494 | 14.3684 | 16.5986 | 20.5815 | 23.7755 | 24.1176 | 24.5934 | 25.4765 | 26.5079 | 29.9223 | 28.1987 | 28.7131 | 27.8553 | 24.2222
278 | 25.1893 | 24.6127 | 24.6381 | 25.0516 | 23.513 | 23.1003 | 22.3939 | 21.3676 | 19.3465 | 18.688 | 20.1996 | 18.0011 | 15.3077 | 14.1728 | 16.6376 | 17.9642 | 21.6462 | 25.7913 | 27.5211 | 28.3922 | 26.4287 | 25.3305 | 24.7547 | 22.177
279 | 21.4539 | 20.0267 | 19.6298 | 18.0047 | 18.0782 | 17.7995 | 18.219 | 18.8316 | 17.4851 | 15.6585 | 14.7731 | 13.709 | 13.3324 | 16.2917 | 16.8786 | 17.2983 | 20.4431 | 25.5524 | 24.6698 | 23.798 | 25.2788 | 27.5673 | 22.7762 | 22.6076
280 | 22.6753 | 20.1826 | 19.5344 | 22.0239 | 24.1362 | 25.9976 | 25.3299 | 23.1194 | 20.859 | 16.5501 | 14.5354 | 13.9728 | 15.5084 | 17.8293 | 18.5235 | 18.2966 | 17.2344 | 18.2689 | 19.6809 | 22.7094 | 24.9613 | 26.0319 | 25.9903 | 25.2403
281 | 25.801 | 24.6555 | 22.1184 | 22.3563 | 22.4065 | 23.6186 | 22.3826 | 20.2347 | 19.2769 | 18.1887 | 15.3842 | 15.848 | 16.6299 | 16.708 | 19.255 | 20.2301 | 21.5766 | 23.1326 | 18.6478 | 19.4039 | 19.687 | 17.0261 | 17.2394 | 17.6863
282 | 21.5124 | 21.0183 | 20.2844 | 19.0535 | 19.1454 | 20.1988 | 19.6907 | 19.6664 | 15.5911 | 13.7159 | 13.2023 | 12.3681 | 12.7709 | 14.7233 | 18.4692 | 20.7416 | 26.2337 | 27.6549 | 27.2162 | 26.6082 | 28.0978 | 27.0671 | 25.5341 | 24.4907
283 | 23.3587 | 23.0238 | 22.8673 | 23.3765 | 22.676 | 22.3265 | 20.5748 | 21.5647 | 18.7557 | 15.8222 | 16.2219 | 14.8948 | 14.6185 | 14.8436 | 16.9852 | 17.1153 | 21.1001 | 19.9944 | 24.452 | 24.0322 | 27.5487 | 30.2798 | 29.2957 | 29.3382
284 | 26.0876 | 26.7113 | 23.9618 | 24.8597 | 26.6091 | 27.4001 | 26.6822 | 25.134 | 22.5205 | 19.0152 | 17.4521 | 14.5612 | 13.6487 | 17.4138 | 18.9529 | 19.9301 | 22.0128 | 25.4598 | 29.25 | 29.3779 | 28.3726 | 27.5178 | 29.3438 | 26.1788
285 | 24.837 | 24.5238 | 23.4522 | 23.7823 | 23.3396 | 25.4263 | 24.0171 | 25.3385 | 23.5999 | 21.673 | 21.4111 | 20.3644 | 17.0971 | 15.9189 | 17.5969 | 19.3804 | 20.7548 | 22.0258 | 23.7249 | 25.0989 | 23.523 | 23.6033 | 27.1691 | 26.686
286 | 25.0699 | 25.9177 | 24.505 | 25.2356 | 25.9564 | 24.7348 | 22.9201 | 19.1085 | 15.7718 | 15.1109 | 14.7381 | 14.9895 | 14.8193 | 15.1123 | 16.205 | 17.6912 | 21.6289 | 22.0363 | 21.4771 | 23.2541 | 23.6614 | 24.0891 | 22.0974 | 22.2533
287 | 22.212 | 22.8892 | 20.493 | 20.8112 | 20.5275 | 21.1255 | 21.0099 | 21.6628 | 21.6074 | 18.3372 | 17.8033 | 17.5066 | 18.438 | 19.2519 | 19.0645 | 22.2552 | 25.4106 | 23.4561 | 23.4396 | 25.065 | 24.0337 | 21.9967 | 21.2084 | 23.0066
288 | 22.6067 | 22.2512 | 21.7307 | 22.763 | 26.2726 | 28.5198 | 27.8355 | 27.3606 | 25.1722 | 21.4792 | 19.5141 | 18.3176 | 17.8089 | 18.3161 | 18.6718 | 19.1485 | 18.1162 | 21.9943 | 25.8564 | 29.1117 | 30.6318 | 27.1556 | 25.8499 | 25.4251
289 | 24.391 | 24.0483 | 22.1644 | 24.4788 | 26.7648 | 28.3095 | 27.6581 | 27.0465 | 28.0982 | 25.735 | 22.6323 | 19.813 | 18.3459 | 19.1841 | 19.2817 | 20.0964 | 24.8056 | 25.5973 | 30.2049 | 28.9113 | 31.5369 | 27.5288 | 26.5393 | 24.0694
290 | 22.9179 | 21.348 | 22.4271 | 22.9254 | 22.1028 | 21.3368 | 21.5261 | 20.799 | 20.2647 | 18.2546 | 17.9177 | 16.0334 | 14.9784 | 16.2187 | 16.6909 | 18.3117 | 20.5641 | 21.3569 | 22.7735 | 25.5386 | 26.8937 | 25.9388 | 24.6528 | 21.6676
291 | 20.3978 | 20.6666 | 21.4466 | 21.5166 | 21.839 | 22.8739 | 22.452 | 22.3048 | 20.4083 | 19.7973 | 20.9976 | 20.9892 | 18.0131 | 18.3294 | 19.5774 | 20.4418 | 22.5232 | 26.0832 | 23.8314 | 23.4812 | 23.4184 | 22.4067 | 22.2388 | 22.862
292 | 22.7379 | 23.9865 | 24.0802 | 22.5197 | 21.968 | 23.6325 | 24.7576 | 24.3716 | 23.4451 | 21.5512 | 20.3781 | 19.359 | 18.3393 | 17.0217 | 15.9476 | 15.3745 | 18.11 | 21.2763 | 21.9418 | 21.6363 | 23.6955 | 21.3373 | 20.3773 | 22.2228
293 | 23.3021 | 24.3419 | 24.6785 | 23.6012 | 23.3232 | 22.9943 | 19.464 | 20.0549 | 20.7102 | 16.8659 | 13.987 | 13.7231 | 13.1899 | 13.2405 | 14.2846 | 15.7471 | 18.1134 | 21.3347 | 24.6231 | 25.2864 | 23.8817 | 21.6998 | 19.3372 | 19.6098
294 | 19.4999 | 19.669 | 20.4001 | 21.477 | 21.7716 | 26.3995 | 26.6957 | 26.3717 | 25.0094 | 22.4983 | 20.1586 | 19.981 | 19.2365 | 19.8935 | 20.23 | 22.6996 | 25.2281 | 26.8375 | 29.6445 | 28.1215 | 28.1827 | 26.4934 | 26.5762 | 26.7044
295 | 26.609 | 26.3038 | 26.5791 | 27.0883 | 26.4026 | 26.079 | 24.6385 | 23.3732 | 23.0128 | 20.7629 | 19.6925 | 18.6434 | 15.261 | 13.157 | 13.8151 | 17.8216 | 20.0755 | 21.7861 | 23.9497 | 25.5924 | 26.358 | 26.1734 | 24.375 | 23.3185
296 | 23.2465 | 23.2717 | 21.826 | 22.2136 | 23.6916 | 24.4231 | 21.8214 | 20.5663 | 18.7716 | 18.0614 | 17.5496 | 15.0468 | 15.4592 | 16.8371 | 16.6587 | 17.4399 | 18.7949 | 20.7745 | 25.0564 | 27.046 | 26.2493 | 22.7154 | 23.1854 | 22.6783
297 | 24.9304 | 25.1038 | 23.2226 | 22.013 | 22.5931 | 22.0436 | 19.4817 | 19.3224 | 19.3918 | 18.0718 | 14.9362 | 14.4496 | 13.9542 | 14.4093 | 15.8184 | 16.7296 | 18.5208 | 21.7717 | 22.7434 | 25.2697 | 24.9255 | 25.3899 | 24.6734 | 22.9663
298 | 21.7891 | 20.8847 | 21.5229 | 23.3119 | 24.4508 | 24.1188 | 23.57 | 25.2234 | 26.1055 | 23.0634 | 19.8019 | 18.7222 | 15.5505 | 15.1772 | 14.1769 | 15.7725 | 19.5316 | 19.9599 | 25.1603 | 30.4632 | 30.8518 | 30.7827 | 28.4846 | 28.1666
299 | 26.262 | 25.7608 | 24.826 | 25.1161 | 25.6608 | 23.0005 | 22.2761 | 23.8185 | 23.9585 | 20.6107 | 18.1545 | 18.881 | 18.4426 | 18.9048 | 18.9245 | 19.7992 | 20.8243 | 22.0726 | 24.2415 | 24.5566 | 24.8876 | 25.8542 | 23.4623 | 24.0525
300 | 25.4673 | 24.4084 | 25.5964 | 27.3792 | 27.6406 | 27.0086 | 27.4522 | 27.4923 | 26.4123 | 21.0299 | 17.3335 | 17.9802 | 16.7542 | 18.7351 | 20.1024 | 22.5756 | 26.196 | 31.7861 | 30.4671 | 30.0731 | 30.2121 | 30.1412 | 24.6624 | 24.8169
301 | 24.8366 | 25.0644 | 25.1776 | 25.5224 | 26.1338 | 29.0782 | 27.3573 | 27.5334 | 27.4104 | 26.3235 | 21.9901 | 19.9877 | 20.3598 | 20.9797 | 21.1239 | 21.4639 | 22.3034 | 23.3694 | 25.4586 | 27.826 | 28.9391 | 27.0699 | 25.5559 | 27.2827
302 | 27.1242 | 28.3366 | 28.6801 | 28.1377 | 28.9739 | 29.5785 | 26.6443 | 26.6147 | 26.3646 | 24.495 | 20.3586 | 21.1911 | 20.2082 | 22.3759 | 25.4645 | 27.2209 | 25.8728 | 27.8449 | 31.3465 | 30.687 | 29.1885 | 31.1352 | 28.9846 | 27.7612
303 | 26.2975 | 26.6606 | 25.6145 | 25.6447 | 26.5734 | 26.4714 | 25.968 | 26.3323 | 25.3662 | 22.3866 | 20.169 | 19.8019 | 18.6706 | 18.2786 | 17.8732 | 20.4643 | 22.2721 | 20.5551 | 25.0365 | 29.1524 | 28.9859 | 27.7667 | 24.3528 | 24.1637
304 | 26.517 | 27.7544 | 26.8255 | 25.4582 | 24.9258 | 25.5641 | 25.0491 | 23.7452 | 23.211 | 19.7563 | 16.5871 | 14.1094 | 15.185 | 17.9815 | 18.3154 | 19.7127 | 21.331 | 26.4953 | 30.6291 | 30.446 | 32.0724 | 29.5608 | 26.1553 | 24.5579
305 | 24.9551 | 26.291 | 26.7753 | 27.4769 | 28.0544 | 29.1906 | 28.2263 | 27.9301 | 26.0883 | 24.9749 | 24.7789 | 24.4163 | 25.3192 | 27.1899 | 25.2247 | 25.9554 | 24.1167 | 22.1816 | 23.8334 | 26.201 | 25.3203 | 24.537 | 25.2892 | 26.1577
306 | 25.4891 | 26.5669 | 26.9367 | 26.3836 | 25.9102 | 25.8734 | 26.1044 | 26.1533 | 24.3749 | 21.6231 | 19.5816 | 17.3593 | 16.5716 | 18.1234 | 18.4136 | 19.2731 | 21.578 | 25.0018 | 25.932 | 25.7295 | 23.445 | 21.0201 | 20.5903 | 18.667
307 | 21.1212 | 20.8855 | 22.1825 | 21.8442 | 22.3613 | 23.6145 | 24.7635 | 23.2386 | 24.08 | 23.4654 | 22.2359 | 20.7388 | 18.2842 | 17.4093 | 15.9901 | 15.4667 | 19.4788 | 22.6442 | 24.2794 | 24.5823 | 24.2902 | 22.3925 | 22.7434 | 23.6747
308 | 23.8894 | 24.4942 | 21.7883 | 21.6631 | 24.1553 | 24.0707 | 22.3713 | 21.4819 | 18.6301 | 15.5925 | 12.4197 | 12.5629 | 13.5967 | 14.9453 | 17.7524 | 18.4427 | 21.5369 | 24.5691 | 29.2428 | 29.742 | 27.7085 | 27.5406 | 26.6554 | 27.7793
309 | 29.0607 | 28.4408 | 27.3992 | 26.8208 | 25.5332 | 24.4713 | 22.1611 | 20.9203 | 21.4974 | 19.4874 | 20.7371 | 18.2466 | 16.5712 | 18.2784 | 16.8594 | 18.9951 | 24.0029 | 25.0965 | 27.2717 | 27.2543 | 26.0819 | 26.2728 | 24.6202 | 24.4552
310 | 24.4252 | 24.8856 | 23.0235 | 24.7278 | 26.3919 | 25.8429 | 24.437 | 24.0249 | 25.3284 | 24.0986 | 22.9711 | 22.9969 | 21.7308 | 21.0516 | 19.1487 | 17.0587 | 18.418 | 21.5382 | 21.7963 | 25.1284 | 25.4958 | 26.6473 | 24.3112 | 24.708
311 | 26.8838 | 28.6864 | 31.424 | 30.9946 | 31.3673 | 30.8235 | 29.9462 | 28.3161 | 27.8306 | 24.2765 | 21.3424 | 19.8453 | 16.8345 | 18.5853 | 19.7376 | 20.8188 | 23.2792 | 27.9675 | 32.7706 | 33.2056 | 34.0843 | 31.9159 | 30.8878 | 30.3557
312 | 30.8789 | 31.0761 | 30.4376 | 30.9945 | 29.721 | 27.139 | 27.2372 | 28.5111 | 29.0724 | 27.423 | 21.5226 | 20.2853 | 19.5593 | 19.8191 | 21.3655 | 23.5078 | 24.3589 | 25.8498 | 27.0217 | 29.3686 | 28.3337 | 29.481 | 27.6742 | 29.0019
313 | 30.49 | 28.6632 | 27.7505 | 28.1031 | 28.6905 | 28.1623 | 23.831 | 20.9851 | 19.922 | 18.7745 | 14.5641 | 14.8958 | 12.9474 | 16.6075 | 18.6734 | 18.219 | 19.7777 | 25.11 | 26.1987 | 28.8959 | 29.2912 | 28.6022 | 24.2804 | 22.2971
314 | 22.1545 | 21.8017 | 21.6254 | 21.4119 | 20.374 | 20.2794 | 21.0526 | 22.8249 | 22.1621 | 20.4411 | 17.4169 | 14.8336 | 15.5542 | 17.5118 | 16.7659 | 15.1686 | 20.0624 | 20.4186 | 21.4061 | 26.339 | 27.2563 | 27.1781 | 25.5825 | 26.1971
315 | 28.6066 | 27.6037 | 25.2136 | 24.9889 | 27.813 | 28.2027 | 26.4865 | 25.4368 | 25.1677 | 23.5125 | 17.6458 | 17.1627 | 14.5974 | 15.0865 | 19.002 | 19.0451 | 19.4788 | 24.4073 | 25.6161 | 27.8714 | 29.3784 | 28.2144 | 25.5129 | 23.738
316 | 25.3728 | 24.6182 | 23.8552 | 24.4094 | 25.7846 | 26.0472 | 23.0906 | 23.885 | 25.2318 | 20.8104 | 17.4273 | 16.8744 | 17.8232 | 16.3113 | 15.1405 | 14.5921 | 19.9321 | 20.7335 | 24.416 | 27.6343 | 27.4048 | 27.6805 | 27.123 | 27.7684
317 | 26.6557 | 29.7209 | 26.1809 | 23.0091 | 24.7246 | 26.9492 | 26.6044 | 26.8308 | 25.7664 | 25.5296 | 25.9516 | 26.2734 | 25.1091 | 23.8734 | 23.7063 | 24.4139 | 24.9689 | 25.9418 | 28.941 | 30.3305 | 30.7329 | 32.4561 | 29.7822 | 27.2588
318 | 26.6194 | 25.068 | 22.7445 | 24.4269 | 24.6075 | 28.104 | 28.0748 | 27.301 | 26.3873 | 26.0215 | 25.9105 | 23.9194 | 21.1568 | 21.9109 | 20.3021 | 21.8996 | 23.0977 | 23.5665 | 25.3136 | 25.7598 | 25.0663 | 24.5089 | 25.0926 | 24.4352
319 | 23.6273 | 25.1486 | 26.7991 | 26.6482 | 27.1879 | 26.3247 | 25.8046 | 25.641 | 22.2778 | 19.4947 | 22.453 | 23.5601 | 21.5617 | 20.8547 | 22.0879 | 22.7768 | 23.3882 | 25.7139 | 24.6762 | 24.0145 | 27.7583 | 26.1547 | 25.0193 | 24.0319
320 | 25.0776 | 26.4463 | 25.0437 | 24.3269 | 23.2165 | 22.2482 | 21.8049 | 21.2496 | 21.7998 | 21.3242 | 17.8501 | 16.8353 | 16.2796 | 15.4261 | 15.9638 | 16.316 | 18.6273 | 23.7645 | 28.7329 | 29.0122 | 31.0472 | 29.5649 | 27.9268 | 28.1148
321 | 30.6722 | 31.57 | 30.2537 | 29.986 | 29.9979 | 30.4215 | 28.7692 | 27.8013 | 25.794 | 24.2501 | 21.7304 | 21.309 | 22.0804 | 21.5189 | 23.8146 | 21.7358 | 20.8389 | 26.2782 | 29.0122 | 31.7088 | 28.4369 | 28.0164 | 25.8046 | 24.0188
322 | 26.1385 | 29.6005 | 31.6463 | 31.5572 | 30.0419 | 30.3838 | 28.49 | 29.2477 | 30.119 | 24.0007 | 20.6754 | 18.3182 | 21.4565 | 23.011 | 21.2314 | 21.5432 | 22.7618 | 26.0294 | 31.2207 | 32.1421 | 31.973 | 30.9727 | 27.1432 | 28.2403
323 | 30.1263 | 29.0495 | 27.1535 | 26.4405 | 26.3591 | 25.333 | 23.3127 | 22.8091 | 22.5026 | 19.6608 | 18.5013 | 17.4127 | 18.0062 | 19.0287 | 18.8253 | 20.6207 | 24.53 | 25.9288 | 26.366 | 27.1398 | 27.486 | 26.0651 | 23.14 | 21.4997
324 | 21.0465 | 21.9589 | 21.3646 | 21.3361 | 24.971 | 24.9459 | 24.2 | 24.2162 | 24.3661 | 22.1917 | 18.1777 | 16.2696 | 15.4317 | 16.6684 | 17.7856 | 17.2803 | 20.2664 | 24.6706 | 26.9147 | 27.3731 | 27.562 | 27.8344 | 23.9736 | 26.0094
325 | 28.0507 | 28.7704 | 28.3077 | 28.3264 | 25.2317 | 25.3876 | 24.9797 | 24.5353 | 23.5943 | 22.5941 | 21.2381 | 22.16 | 23.3827 | 23.6595 | 22.3079 | 22.9332 | 24.6612 | 24.9419 | 29.2007 | 30.2883 | 29.9027 | 27.6008 | 27.0429 | 28.5221
326 | 31.153 | 31.6603 | 32.9638 | 34.3139 | 34.0204 | 31.7104 | 31.9238 | 31.1071 | 29.9412 | 28.156 | 22.9336 | 18.0702 | 15.0648 | 17.5649 | 21.9247 | 22.6425 | 22.8782 | 24.7623 | 25.9582 | 25.2876 | 26.4386 | 24.0289 | 21.5 | 20.9502
327 | 22.8878 | 23.3149 | 22.7475 | 21.4895 | 20.9893 | 20.7681 | 20.9412 | 22.8521 | 22.1165 | 18.1402 | 20.2745 | 19.4486 | 19.9235 | 20.9456 | 21.5852 | 22.9635 | 23.6892 | 21.4005 | 22.7427 | 24.961 | 30.5585 | 30.3083 | 30.1141 | 29.981
328 | 30.035 | 29.5474 | 27.9819 | 27.8304 | 28.8864 | 29.7757 | 29.8661 | 29.0674 | 27.5747 | 27.0207 | 25.417 | 24.231 | 22.6962 | 20.75 | 19.5649 | 22.9574 | 26.4579 | 27.5175 | 27.886 | 29.025 | 28.6296 | 26.9322 | 27.3463 | 28.2197
329 | 27.9355 | 28.7949 | 31.4804 | 30.6881 | 31.2044 | 30.3624 | 29.6091 | 27.7676 | 28.0122 | 26.0022 | 24.1735 | 22.203 | 20.6005 | 20.4926 | 19.8683 | 21.1394 | 22.9757 | 25.9189 | 29.962 | 33.8222 | 32.3374 | 30.9413 | 30.8735 | 30.6503
330 | 29.5546 | 27.5029 | 26.5731 | 26.2284 | 26.3436 | 26.7295 | 24.0433 | 23.5455 | 22.9181 | 21.6095 | 19.6916 | 20.6906 | 24.5207 | 25.1269 | 22.4491 | 20.4763 | 21.0987 | 21.7383 | 23.2083 | 23.9251 | 25.7319 | 24.3487 | 23.9799 | 22.1163
331 | 22.2536 | 24.8404 | 26.0487 | 26.1839 | 27.4796 | 28.2977 | 27.2096 | 25.6111 | 25.3206 | 22.8435 | 21.5555 | 20.3384 | 19.7725 | 20.9387 | 21.6535 | 22.6231 | 23.6085 | 24.4922 | 26.985 | 28.6634 | 28.4326 | 27.1048 | 26.5471 | 26.2966
332 | 26.8919 | 27.4543 | 28.9359 | 30.1942 | 30.7775 | 30.9058 | 30.0836 | 29.8345 | 28.1065 | 24.1851 | 21.7184 | 20.3322 | 18.9539 | 20.5411 | 22.6203 | 24.955 | 29.1579 | 28.3488 | 29.3892 | 29.9595 | 28.8303 | 27.7121 | 24.2714 | 23.7625
333 | 22.4462 | 21.7141 | 23.0599 | 25.0542 | 23.8663 | 25.4475 | 28.0061 | 27.93 | 26.9169 | 25.167 | 26.3775 | 27.7981 | 27.0185 | 25.6737 | 25.0465 | 25.9682 | 25.1744 | 27.3764 | 28.2992 | 28.5933 | 26.4819 | 26.548 | 29.0656 | 29.4901
334 | 28.3378 | 28.7198 | 29.7963 | 28.8352 | 27.6359 | 28.2533 | 27.953 | 26.378 | 27.5822 | 26.6972 | 23.9931 | 22.5093 | 22.4562 | 22.6386 | 21.6429 | 23.3648 | 25.1643 | 26.9807 | 30.0715 | 29.5572 | 28.369 | 28.0281 | 25.5377 | 25.9484
335 | 29.5302 | 32.131 | 32.8796 | 31.8276 | 30.9739 | 29.2069 | 27.3173 | 26.7095 | 25.1853 | 23.5017 | 22.7926 | 22.1798 | 20.47 | 20.2244 | 23.4838 | 23.9018 | 24.6269 | 28.9305 | 29.3349 | 32.4967 | 31.5437 | 30.5283 | 30.1432 | 29.3321
336 | 30.8015 | 31.1252 | 30.7969 | 31.7258 | 30.015 | 29.3993 | 28.7349 | 27.1519 | 27.0476 | 25.815 | 23.0973 | 22.6783 | 23.5322 | 23.9175 | 24.0213 | 24.3917 | 26.1788 | 29.2883 | 32.6711 | 32.3688 | 29.3655 | 28.6837 | 26.8432 | 27.7322
337 | 28.6075 | 26.392 | 23.1414 | 23.2215 | 21.9279 | 22.2657 | 21.0143 | 20.6948 | 21.5959 | 22.1082 | 20.8684 | 18.4201 | 17.6744 | 18.3065 | 19.1344 | 19.252 | 20.6584 | 22.7312 | 24.8649 | 25.8343 | 24.8492 | 24.5196 | 23.2658 | 21.4362
338 | 21.2321 | 22.2315 | 22.9159 | 19.8663 | 18.7261 | 19.1796 | 19.6132 | 21.4471 | 22.4316 | 22.4504 | 21.3024 | 19.5943 | 19.5615 | 20.0497 | 19.8942 | 23.5278 | 25.073 | 24.6692 | 24.047 | 24.1669 | 24.2097 | 24.2012 | 23.6568 | 24.3575
339 | 24.4776 | 25.224 | 25.3936 | 25.4408 | 27.5943 | 28.9528 | 28.067 | 26.8896 | 27.6739 | 27.179 | 27.2492 | 24.3033 | 20.5296 | 18.5787 | 18.2314 | 16.5347 | 16.0839 | 17.7238 | 20.8393 | 22.9433 | 25.5182 | 28.2533 | 28.7203 | 27.3852
340 | 25.7107 | 25.8247 | 26.7591 | 27.5802 | 26.0035 | 26.1112 | 23.3593 | 20.7751 | 19.6374 | 18.4464 | 16.5944 | 13.5063 | 14.1336 | 15.0374 | 15.938 | 17.7989 | 19.8343 | 21.2976 | 26.504 | 26.785 | 27.1093 | 28.2745 | 27.5388 | 24.6733
341 | 24.8334 | 25.8827 | 26.925 | 27.4133 | 27.9923 | 27.0723 | 24.7396 | 24.6365 | 25.079 | 24.8962 | 22.1944 | 20.8243 | 19.8033 | 19.2187 | 20.254 | 22.6679 | 23.6004 | 20.5519 | 21.354 | 22.1928 | 22.8399 | 23.0715 | 23.3576 | 22.7818
342 | 22.8478 | 25.3441 | 23.168 | 22.8994 | 24.5646 | 24.4639 | 25.1395 | 24.5175 | 24.0712 | 22.1606 | 21.7163 | 22.7959 | 22.8623 | 22.518 | 23.438 | 22.7183 | 21.3127 | 20.2541 | 23.7575 | 26.576 | 26.0312 | 26.3527 | 23.703 | 22.0911
343 | 22.7683 | 26.4194 | 28.1873 | 28.7928 | 30.4052 | 30.631 | 30.915 | 31.1901 | 31.4912 | 30.4172 | 28.338 | 25.8224 | 23.0625 | 23.0316 | 23.1905 | 22.863 | 23.054 | 26.3731 | 26.6317 | 29.5172 | 30.2374 | 28.4227 | 27.5615 | 26.6659
344 | 25.7977 | 25.7687 | 27.7199 | 27.4908 | 26.546 | 25.0348 | 24.5976 | 24.1229 | 23.8997 | 24.3985 | 25.2116 | 23.4209 | 22.2891 | 21.6346 | 22.8355 | 22.4994 | 23.3564 | 23.1473 | 25.1308 | 24.3284 | 25.4915 | 27.7672 | 25.4228 | 23.3637
345 | 23.6543 | 25.2044 | 27.2487 | 27.7548 | 27.0029 | 26.7551 | 26.0756 | 24.1386 | 24.0087 | 24.914 | 22.9855 | 22.2197 | 21.2436 | 19.8286 | 17.7529 | 18.9199 | 19.1457 | 19.5837 | 23.3832 | 22.4552 | 21.152 | 24.6688 | 25.9901 | 24.9207
346 | 22.3956 | 24.2163 | 25.1271 | 24.8216 | 24.6828 | 23.8848 | 23.6954 | 23.8656 | 23.9145 | 23.1171 | 20.225 | 20.798 | 20.6869 | 20.9613 | 23.2886 | 23.6156 | 22.0572 | 21.3231 | 25.0376 | 27.3805 | 27.3998 | 28.141 | 26.9975 | 28.3243
347 | 30.21 | 31.149 | 33.8634 | 34.574 | 33.2503 | 31.9066 | 30.1992 | 26.6031 | 26.4174 | 27.1082 | 24.698 | 24.1218 | 24.4495 | 24.5085 | 22.0758 | 20.5809 | 20.0729 | 24.6363 | 29.6151 | 31.4776 | 33.6666 | 32.372 | 31.4763 | 34.2859
348 | 33.2697 | 32.4326 | 33.2212 | 30.1011 | 27.4624 | 29.0399 | 30.4714 | 29.7999 | 31.309 | 30.3924 | 27.4743 | 27.3247 | 26.856 | 22.3772 | 23.2125 | 22.0273 | 24.1901 | 27.3174 | 32.2677 | 34.0253 | 32.3323 | 31.537 | 31.4679 | 28.5889
349 | 26.6801 | 26.6144 | 27.1253 | 26.3512 | 26.3498 | 25.8387 | 24.4459 | 23.817 | 25.2373 | 25.4422 | 24.4021 | 23.3354 | 27.0296 | 26.7163 | 26.8381 | 25.0216 | 22.5231 | 24.5393 | 26.4945 | 27.7395 | 26.8024 | 25.6965 | 25.4238 | 23.6199
350 | 26.5274 | 28.3859 | 32.1419 | 33.0045 | 29.5069 | 26.6527 | 25.9069 | 23.8814 | 21.1734 | 20.1956 | 19.9342 | 19.0088 | 19.7743 | 21.1745 | 21.2613 | 20.2625 | 20.4561 | 23.0415 | 27.9973 | 27.5358 | 27.7941 | 26.6745 | 23.5315 | 21.5205
351 | 23.5485 | 25.6991 | 26.8757 | 25.9923 | 23.3612 | 23.2928 | 23.0767 | 21.5382 | 21.9278 | 22.241 | 20.5095 | 20.092 | 21.7989 | 22.2513 | 21.806 | 22.1492 | 22.9962 | 22.1184 | 21.8671 | 23.4891 | 23.6606 | 23.8641 | 24.2929 | 24.0541
352 | 23.8893 | 23.584 | 24.8863 | 25.6404 | 26.922 | 27.8736 | 26.9039 | 27.6848 | 27.9383 | 27.5738 | 27.0517 | 25.6355 | 24.2102 | 25.0437 | 23.1679 | 22.5535 | 21.6798 | 24.2746 | 25.7971 | 26.68 | 27.6398 | 28.0524 | 28.3945 | 26.8809
353 | 24.3417 | 24.9079 | 27.2143 | 26.9435 | 26.7005 | 26.0264 | 25.2402 | 26.337 | 27.5638 | 29.0764 | 25.969 | 22.9423 | 21.9829 | 22.3775 | 25.2958 | 25.105 | 26.3866 | 25.7103 | 24.4134 | 24.0111 | 23.278 | 23.1813 | 23.9583 | 24.8659
354 | 25.1955 | 26.4548 | 27.7527 | 26.8017 | 26.637 | 27.4955 | 27.0996 | 25.2496 | 24.8795 | 23.3432 | 20.4837 | 18.253 | 19.8719 | 22.0203 | 21.8369 | 23.3557 | 23.3291 | 24.4987 | 27.6921 | 28.6549 | 27.8852 | 29.3942 | 30.0146 | 29.4856
355 | 30.0387 | 30.6169 | 30.2846 | 28.2708 | 28.513 | 28.9898 | 28.527 | 28.1917 | 27.0417 | 24.357 | 22.0793 | 21.0799 | 22.6455 | 23.6503 | 24.7837 | 22.5189 | 20.9874 | 23.4528 | 25.8937 | 26.2832 | 23.2731 | 25.5566 | 26.2625 | 25.1545
356 | 25.4881 | 26.5603 | 26.4437 | 26.5244 | 25.4611 | 25.4359 | 22.0611 | 20.0239 | 20.02 | 20.237 | 19.809 | 19.1309 | 19.842 | 22.4056 | 21.6178 | 22.5201 | 24.2921 | 25.2105 | 25.2804 | 24.645 | 26.5155 | 27.2362 | 26.6223 | 27.5797
357 | 27.5708 | 27.6262 | 26.6034 | 25.225 | 24.2903 | 23.0302 | 21.5819 | 22.4415 | 22.5715 | 22.4809 | 21.7647 | 19.5663 | 18.8858 | 20.9811 | 22.5274 | 21.2685 | 20.1251 | 21.0423 | 24.9347 | 25.3996 | 23.9736 | 22.5243 | 22.8371 | 22.2012
358 | 22.8322 | 23.9308 | 24.211 | 24.8876 | 25.7146 | 26.1657 | 24.2697 | 24.061 | 24.3394 | 23.4638 | 21.794 | 19.0547 | 18.9785 | 18.1278 | 17.9843 | 17.7039 | 18.6038 | 20.0954 | 21.9668 | 23.2022 | 24.6872 | 23.8542 | 23.3817 | 20.9018
359 | 21.5064 | 24.8442 | 27.4714 | 27.5723 | 24.9636 | 22.6196 | 20.4621 | 19.9471 | 19.8258 | 20.5923 | 18.2284 | 18.1128 | 20.3761 | 19.9033 | 20.051 | 19.2635 | 19.8428 | 21.7998 | 25.0773 | 24.0475 | 24.9689 | 26.5533 | 27.2257 | 26.806
360 | 27.1278 | 27.1476 | 28.2188 | 28.8442 | 28.972 | 30.7681 | 30.1089 | 31.3123 | 30.2032 | 28.3688 | 26.0191 | 25.8847 | 25.773 | 25.0959 | 25.5012 | 25.5526 | 23.1021 | 24.1407 | 28.8912 | 24.2972 | 24.0317 | 23.3421 | 26.8562 | 27.7201
361 | 26.2013 | 26.7517 | 27.0701 | 24.4918 | 23.7599 | 23.7857 | 23.9615 | 23.589 | 22.4323 | 22.078 | 20.6408 | 19.8622 | 20.8567 | 22.0699 | 23.4469 | 24.2425 | 25.5915 | 28.358 | 29.7331 | 30.9467 | 31.8693 | 30.6992 | 29.1217 | 29.3214
362 | 30.94 | 31.0718 | 30.5634 | 30.3795 | 29.3747 | 28.9628 | 26.3268 | 24.725 | 26.3469 | 24.5757 | 20.3545 | 17.7938 | 17.3133 | 14.8722 | 14.6759 | 14.3488 | 16.4313 | 18.2017 | 21.189 | 24.2108 | 24.1313 | 25.1421 | 25.6288 | 26.5724
363 | 28.6364 | 30.0459 | 31.6571 | 30.16 | 28.9895 | 29.393 | 28.3529 | 26.647 | 26.6874 | 26.1488 | 22.6883 | 18.2423 | 17.325 | 17.9856 | 18.1495 | 19.2219 | 22.2068 | 24.3567 | 26.5412 | 29.307 | 30.3022 | 30.9694 | 30.7833 | 31.3753
364 | 31.7699 | 32.7901 | 32.9304 | 31.8572 | 30.2012 | 30.5003 | 30.8714 | 31.285 | 31.7211 | 30.836 | 25.8559 | 22.7532 | 22.0202 | 22.4976 | 22.4536 | 20.6455 | 22.9477 | 25.6992 | 27.2353 | 27.8701 | 27.088 | 25.2102 | 22.7537 | 20.3852
365 | 22.0462 | 23.458 | 23.65 | 23.4471 | 23.8333 | 23.357 | 22.738 | 20.7591 | 20.501 | 20.8662 | 19.2675 | 18.4502 | 17.3419 | 15.0583 | 14.1537 | 15.3007 | 18.4859 | 21.7514 | 26.6634 | 28.014 | 25.7805 | 23.7694 | 21.73 | 21.8221
8760 - Energy Profile
version 1-1
CLIENT: BLACK HILLS CORP.
PROJECT: BUSCH RANCH II
TURBINE: VESTAS V120-2.2MW
HUB HEIGHT: 80M
ALL DATA PRESENTED IN THIS PRELIMINARY REPORT ARE DRAFT AND ARE SUBJECT TO CHANGE DURING THE FINAL QUALITY CONTROL PROCESS.

## 8760-TMY
Date are in local time (UTC -7)
Values represent a "typical meterological year" in that the sum if the year is equal to the annual P50, but the hour to hour variability is more realistic.
MWh | HOUR
DAY | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
1 | 32.5219 | 42.4935 | 58.4452 | 59.3667 | 59.0781 | 59.0587 | 59.2155 | 59.0523 | 53.4506 | 39.2039 | 26.1643 | 14.8113 | 2.7217 | 0 | 0 | 0.15051 | 16.597 | 51.5511 | 58.7523 | 58.072 | 58.2829 | 59.4 | 59.3384 | 49.2918
2 | 59.1527 | 52.4715 | 54.8419 | 58.9536 | 56.5034 | 58.4334 | 58.3192 | 45.1954 | 7.6053 | 0 | 20.9146 | 52.8997 | 56.8001 | 59.0679 | 58.1258 | 44.5909 | 58.2654 | 58.1135 | 59.3075 | 59.2685 | 58.8591 | 59.3444 | 59.4 | 59.4
3 | 59.4 | 58.987 | 52.2621 | 44.1553 | 52.8074 | 20.2224 | 25.7836 | 53.9715 | 20.2706 | 10.8494 | 21.6355 | 42.2242 | 58.5887 | 48.9279 | 41.992 | 41.2539 | 15.5993 | 4.1778 | 6.727 | 3.2579 | 3.7763 | 7.7475 | 12.3049 | 3.827
4 | 0 | 0.56451 | 2.5079 | 1.1231 | 0.40165 | 2.339 | 4.2456 | 5.583 | 9.8157 | 10.2271 | 16.1074 | 30.2593 | 29.8532 | 30.8343 | 16.6284 | 10.2185 | 24.389 | 59.4 | 59.2921 | 44.4754 | 25.6626 | 56.5525 | 59.3721 | 59.3665
5 | 56.1845 | 29.1102 | 16.7379 | 14.3688 | 18.5417 | 16.5778 | 24.8461 | 35.3945 | 28.3619 | 16.5276 | 49.2754 | 59.4 | 59.1866 | 59.4 | 57.839 | 48.2836 | 35.3211 | 31.1327 | 21.9767 | 0.12893 | 0 | 1.0055 | 6.2594 | 16.3413
6 | 39.2735 | 57.3114 | 58.3001 | 57.951 | 51.2616 | 44.6924 | 46.0907 | 44.2923 | 41.6239 | 31.9372 | 15.5338 | 6.1047 | 1.8894 | 0.84038 | 0.86368 | 1.3541 | 5.3377 | 11.957 | 20.2743 | 6.5664 | 15.2514 | 23.7438 | 38.7201 | 42.0997
7 | 33.2515 | 24.2309 | 21.7356 | 20.8774 | 26.2172 | 24.4474 | 16.0055 | 12.696 | 18.3301 | 34.5919 | 13.6634 | 16.3061 | 18.9792 | 21.1965 | 13.9154 | 12.3253 | 19.8048 | 56.6214 | 47.7711 | 46.3946 | 52.5868 | 55.1578 | 58.3965 | 58.9811
8 | 58.361 | 59.4 | 59.3437 | 59.2295 | 58.7692 | 59.1621 | 59.3742 | 59.4 | 59.4 | 58.5891 | 50.6422 | 35.9204 | 26.2595 | 22.2508 | 23.1773 | 14.9886 | 0.061225 | 0 | 0.87135 | 9.6088 | 1.5739 | 0.14462 | 12.1918 | 14.0286
9 | 10.9537 | 9.6901 | 11.1274 | 14.1961 | 26.9996 | 40.0118 | 31.5747 | 31.5621 | 31.3635 | 27.2529 | 17.2607 | 10.0269 | 3.9249 | 3.1581 | 2.8843 | 2.0128 | 1.8873 | 3.7851 | 5.9186 | 7.4957 | 5.5053 | 3.5504 | 4.0752 | 5.9079
10 | 4.388 | 1.8552 | 3.1302 | 3.5335 | 4.1161 | 4.9023 | 4.9767 | 4.4743 | 0 | 0 | 0.038518 | 1.752 | 4.1623 | 6.6782 | 8.8049 | 7.6625 | 6.0129 | 4.1102 | 1.743 | 0.085596 | 0.03727 | 0.8833 | 1.3699 | 0.91367
11 | 0.082742 | 1.9596 | 6.6614 | 10.9643 | 15.9663 | 12.8728 | 9.2005 | 8.3668 | 5.1468 | 3.694 | 8.8819 | 11.3595 | 9.7467 | 12.3258 | 13.0131 | 11.0248 | 3.7402 | 0.1187 | 0 | 0 | 0 | 0 | 0 | 0
12 | 0 | 1.3137 | 2.4367 | 3.2268 | 4.3991 | 6.7538 | 11.6744 | 22.2082 | 27.7646 | 17.283 | 12.6938 | 9.9558 | 2.3676 | 0 | 0 | 0 | 0.56874 | 17.388 | 42.5765 | 59.4 | 52.1308 | 18.8257 | 10.3215 | 22.6211
13 | 58.9065 | 59.2675 | 54.1971 | 52.8252 | 56.1524 | 49.2824 | 43.2981 | 37.8609 | 23.6102 | 11.4297 | 2.9419 | 0 | 0 | 0 | 0.031266 | 4.4946 | 5.5848 | 4.877 | 1.2555 | 11.2656 | 13.3791 | 7.4339 | 29.4271 | 17.1358
14 | 4.446 | 7.3183 | 8.2069 | 3.58 | 6.555 | 4.9425 | 3.0106 | 3.8251 | 8.1159 | 10.5344 | 11.437 | 4.1395 | 0.17589 | 0 | 0.20763 | 1.1283 | 0.34803 | 0.97858 | 0.77333 | 10.3178 | 16.8884 | 54.2567 | 59.4 | 59.3201
15 | 59.1952 | 59.4 | 59.157 | 57.4147 | 55.6301 | 55.5467 | 57.0474 | 54.9866 | 55.9082 | 56.6009 | 57.6696 | 59.1421 | 54.2037 | 36.6421 | 50.4151 | 55.1073 | 55.3349 | 8.1795 | 14.8494 | 36.5178 | 47.6139 | 34.9117 | 33.9033 | 18.0463
16 | 20.769 | 21.554 | 19.2016 | 42.61 | 54.6344 | 53.8034 | 57.0516 | 42.7275 | 27.0919 | 56.7112 | 59.4 | 59.4 | 59.4 | 59.4 | 58.4042 | 42.2584 | 20.6721 | 9.2505 | 0.49556 | 5.7786 | 17.5195 | 18.539 | 10.9711 | 15.0482
17 | 20.7757 | 23.2855 | 26.1867 | 36.8036 | 44.2506 | 43.0062 | 49.5739 | 52.6033 | 54.2252 | 52.1588 | 41.4621 | 32.9541 | 29.1304 | 53.2398 | 59.2577 | 59.4 | 59.4 | 50.0429 | 46.1361 | 45.487 | 45.715 | 44.9508 | 49.1047 | 58.2966
18 | 59.4 | 59.3903 | 57.8998 | 51.8581 | 50.6318 | 43.4397 | 36.3728 | 34.2952 | 30.8865 | 19.4598 | 15.8792 | 22.4226 | 51.0132 | 40.8089 | 27.995 | 15.2688 | 20.299 | 15.5378 | 52.9604 | 59.4 | 59.4 | 59.4 | 59.3888 | 59.2209
19 | 59.4 | 59.3657 | 59.3902 | 59.4 | 59.4 | 58.558 | 38.552 | 26.2979 | 23.5639 | 10.6531 | 0.75277 | 0.59661 | 7.2549 | 21.7353 | 30.1682 | 14.4851 | 10.859 | 7.182 | 7.2065 | 8.1042 | 9.3668 | 11.3827 | 7.0504 | 6.6982
20 | 5.4452 | 7.964 | 6.1486 | 5.5824 | 4.6144 | 2.4597 | 2.1556 | 1.077 | 2.3372 | 1.2777 | 0.58175 | 1.7494 | 2.6577 | 2.9011 | 3.32 | 3.4662 | 3.8479 | 4.6952 | 6.7006 | 6.1639 | 7.8763 | 9.6733 | 9.3599 | 7.8143
21 | 7.9303 | 8.0165 | 8.8843 | 9.7566 | 12.3613 | 10.1617 | 6.84 | 6.5433 | 6.0718 | 5.4105 | 5.9646 | 9.2576 | 14.1786 | 18.7231 | 21.3538 | 20.7502 | 23.5334 | 26.1371 | 22.8804 | 16.198 | 11.5619 | 9.6162 | 9.35 | 8.0228
22 | 23.2721 | 26.1986 | 13.0632 | 3.1955 | 4.1808 | 1.4917 | 0.077333 | 0 | 0.6428 | 2.2903 | 7.7034 | 21.9576 | 25.0266 | 24.2441 | 20.812 | 11.0037 | 5.6309 | 0.78213 | 0 | 0.043689 | 4.5112 | 6.7934 | 22.1038 | 25.1325
23 | 30.1181 | 36.8298 | 42.4213 | 49.4453 | 51.352 | 48.2386 | 58.7743 | 27.3496 | 5.9961 | 2.8763 | 1.9037 | 0 | 0 | 0 | 5.1628 | 19.2174 | 34.1783 | 56.5118 | 59.4 | 58.8969 | 59.2675 | 10.5485 | 3.5031 | 4.122
24 | 1.2801 | 1.9198 | 16.0961 | 22.0547 | 54.6466 | 59.2445 | 59.3675 | 58.282 | 59.2934 | 45.26 | 16.7776 | 14.4734 | 7.6711 | 3.6961 | 1.3301 | 0.26784 | 0.031563 | 0.15342 | 2.7283 | 12.9725 | 26.3139 | 24.4031 | 34.5324 | 52.0406
25 | 38.566 | 31.0592 | 43.8998 | 45.14 | 45.7001 | 37.1993 | 26.0575 | 20.0022 | 19.8038 | 12.6528 | 12.9084 | 57.1561 | 55.203 | 27.4139 | 25.5884 | 16.9759 | 14.8557 | 2.4131 | 58.8395 | 59.4 | 17.8426 | 19.2927 | 11.1245 | 12.7394
26 | 9.1873 | 12.8141 | 20.6442 | 25.8492 | 27.2069 | 16.8617 | 11.6128 | 8.5944 | 7.9136 | 6.0192 | 0.40408 | 0 | 0 | 0 | 0.95617 | 0 | 5.6249 | 36.9718 | 59.1493 | 48.8823 | 29.9939 | 16.9466 | 7.3293 | 1.5742
27 | 3.8183 | 11.7749 | 32.8141 | 47.205 | 53.8523 | 47.2411 | 41.5184 | 40.4336 | 42.1209 | 38.4503 | 26.692 | 37.3638 | 27.9872 | 15.3667 | 26.2976 | 56.5439 | 59.4 | 59.4 | 59.4 | 59.1901 | 42.98 | 9.4922 | 5.4448 | 15.4073
28 | 41.4784 | 44.3966 | 34.2228 | 43.6044 | 30.969 | 20.8796 | 23.9492 | 44.7071 | 51.018 | 25.8984 | 5.8382 | 0 | 0 | 0 | 0 | 0 | 3.2084 | 32.4668 | 27.4225 | 7.0126 | 4.3191 | 2.5578 | 2.3607 | 0.46608
29 | 0 | 0 | 0.39802 | 0.21696 | 0 | 3.1852 | 34.5916 | 52.0848 | 49.3121 | 33.6988 | 9.2623 | 0.99124 | 0 | 0 | 0 | 0 | 2.0117 | 12.5004 | 56.5906 | 59.4 | 59.2864 | 58.6302 | 59.0732 | 58.8302
30 | 52.0864 | 32.5225 | 9.243 | 6.5064 | 8.6276 | 29.7109 | 32.4426 | 32.8451 | 30.9429 | 23.6618 | 27.3762 | 30.7283 | 26.0225 | 22.9379 | 13.5912 | 7.1172 | 1.8776 | 0 | 0.99368 | 0 | 2.7575 | 6.8214 | 20.5866 | 4.8229
31 | 12.9881 | 35.3219 | 36.0661 | 38.4902 | 30.3789 | 22.91 | 21.0291 | 16.4338 | 19.4663 | 7.9207 | 1.3035 | 1.2426 | 4.3008 | 7.1715 | 6.1656 | 5.0268 | 7.2443 | 10.0244 | 0 | 2.4703 | 12.8176 | 4.1418 | 0 | 0
32 | 11.0037 | 19.7829 | 55.7598 | 55.3069 | 54.7431 | 55.076 | 51.3535 | 49.1757 | 38.0424 | 20.9968 | 27.7478 | 58.523 | 40.9184 | 21.1522 | 14.6778 | 8.6941 | 0.74421 | 0.25292 | 14.0142 | 42.2232 | 38.8561 | 20.9214 | 16.8733 | 15.3661
33 | 18.5296 | 18.4331 | 11.9463 | 7.2407 | 3.7184 | 0.102 | 3.6628 | 13.2091 | 38.4381 | 23.4431 | 17.0782 | 17.6783 | 16.0398 | 18.1396 | 14.9578 | 8.7315 | 12.0544 | 28.7557 | 58.9745 | 58.874 | 59.0183 | 57.2196 | 40.9602 | 27.9148
34 | 13.2641 | 1.9959 | 0 | 0.12465 | 11.7747 | 24.4612 | 23.9596 | 33.1707 | 25.6818 | 24.785 | 12.137 | 8.6501 | 7.4375 | 6.5322 | 5.4903 | 9.9532 | 22.9266 | 4.3855 | 4.6516 | 6.0711 | 13.7115 | 24.1098 | 24.7212 | 24.988
35 | 23.4339 | 21.8728 | 20.9838 | 11.5616 | 30.2141 | 34.229 | 17.6743 | 9.9316 | 4.5369 | 2.2148 | 2.3526 | 10.5361 | 22.6182 | 21.5757 | 4.9635 | 0 | 11.5103 | 9.6129 | 30.8285 | 58.9471 | 59.1116 | 59.053 | 58.3159 | 54.5237
36 | 43.3708 | 33.9432 | 23.1967 | 18.1277 | 16.6123 | 11.2526 | 6.7194 | 12.9235 | 18.2985 | 5.1404 | 0.62265 | 2.2523 | 1.0087 | 0 | 0.76127 | 7.8314 | 24.8685 | 34.4008 | 31.8494 | 29.8059 | 18.2899 | 11.8205 | 10.0501 | 16.7852
37 | 10.989 | 15.6808 | 11.7878 | 9.5375 | 6.1583 | 3.0693 | 0.53129 | 0.037686 | 0.041371 | 0 | 2.7049 | 5.6658 | 6.1752 | 9.7055 | 10.7736 | 12.2818 | 10.7487 | 10.573 | 8.3468 | 8.6285 | 1.9018 | 0.821 | 1.9188 | 0.99743
38 | 6.173 | 8.4695 | 7.9391 | 6.222 | 6.1179 | 4.0232 | 4.2033 | 6.3031 | 5.1309 | 4.9803 | 7.1336 | 11.4196 | 19.1257 | 27.6789 | 32.5259 | 33.836 | 30.4758 | 24.2805 | 12.2072 | 8.2364 | 5.9428 | 3.0744 | 1.2065 | 0
39 | 37.3108 | 32.5968 | 33.4475 | 54.6951 | 58.1009 | 58.0462 | 59.166 | 59.399 | 59.4 | 59.4 | 59.4 | 58.092 | 51.4177 | 58.4991 | 53.1656 | 56.8079 | 58.4493 | 55.9724 | 52.42 | 46.8863 | 58.7907 | 59.1231 | 55.4604 | 36.6426
40 | 30.6237 | 38.2036 | 43.0659 | 38.589 | 31.2244 | 25.3446 | 34.9331 | 22.638 | 9.0157 | 5.0139 | 3.1477 | 0 | 2.7323 | 9.9947 | 6.1772 | 19.419 | 23.1213 | 13.45 | 16.7153 | 13.59 | 13.8346 | 22.0619 | 53.5824 | 59.1957
41 | 50.0487 | 38.1106 | 47.5879 | 58.5898 | 59.3962 | 58.8674 | 55.3756 | 59.4 | 59.4 | 58.8656 | 56.5855 | 41.0652 | 26.9561 | 26.703 | 10.0822 | 1.1788 | 0 | 0 | 0 | 0 | 3.6723 | 11.0103 | 12.1248 | 21.7797
42 | 37.5443 | 49.8528 | 57.9272 | 59.3094 | 59.3819 | 59.0273 | 58.8684 | 58.9562 | 59.3926 | 59.4 | 59.1501 | 51.0143 | 43.4224 | 43.1649 | 51.7842 | 51.3143 | 47.6552 | 16.3637 | 44.4788 | 51.1043 | 55.7702 | 55.7012 | 58.8674 | 58.6626
43 | 57.3417 | 58.2034 | 55.7482 | 37.6976 | 28.4804 | 7.1198 | 2.3322 | 9.959 | 6.7719 | 16.614 | 10.0649 | 7.2325 | 5.0645 | 0.97252 | 0 | 0 | 2.5121 | 11.8452 | 29.5392 | 58.4135 | 56.3081 | 58.1497 | 32.9892 | 13.8537
44 | 11.6461 | 8.2325 | 12.5178 | 19.0421 | 17.6783 | 29.2404 | 47.2901 | 37.423 | 23.1993 | 17.632 | 7.004 | 10.2026 | 5.906 | 0 | 0 | 0 | 0.086071 | 1.9378 | 11.0847 | 18.4097 | 28.4806 | 52.7848 | 21.0884 | 11.6456
45 | 22.8552 | 57.7515 | 59.4 | 56.3072 | 47.5742 | 50.5297 | 48.4654 | 57.3481 | 59.3757 | 59.3831 | 58.7875 | 59.4 | 59.4 | 59.2007 | 59.4 | 59.4 | 59.372 | 58.646 | 58.4387 | 59.4 | 59.3671 | 59.3791 | 59.4 | 59.4
46 | 59.4 | 59.4 | 57.1711 | 59.4 | 56.7844 | 37.3798 | 40.4894 | 51.4031 | 40.1232 | 32.5697 | 24.3467 | 26.4641 | 18.1048 | 10.5378 | 14.1311 | 11.581 | 20.2837 | 26.6085 | 23.1362 | 37.1069 | 24.7096 | 9.0954 | 3.2343 | 3.7984
47 | 9.4188 | 10.3482 | 6.9167 | 4.8995 | 13.9826 | 5.0033 | 4.0779 | 6.8434 | 11.2844 | 13.1958 | 21.6597 | 18.046 | 18.2167 | 25.1104 | 27.1414 | 6.9576 | 43.9634 | 41.913 | 23.235 | 18.5581 | 6.5292 | 5.4621 | 2.0827 | 0
48 | 0 | 0.078403 | 2.7805 | 1.4129 | 3.1978 | 7.2157 | 6.5574 | 5.8884 | 3.9914 | 2.4458 | 1.348 | 0.71954 | 0.078284 | 3.3857 | 3.2406 | 5.5223 | 9.2849 | 18.9412 | 21.0513 | 22.4169 | 16.113 | 9.1558 | 10.2274 | 7.8979
49 | 6.0957 | 6.7015 | 9.675 | 8.4248 | 8.293 | 10.3193 | 15.814 | 11.6362 | 10.1093 | 22.8886 | 23.4631 | 23.7849 | 40.4453 | 29.8479 | 21.6329 | 16.5135 | 10.6597 | 4.1417 | 0 | 0 | 0 | 1.2861 | 2.9236 | 0.71294
50 | 5.4183 | 13.6363 | 16.5999 | 18.4 | 17.1055 | 6.284 | 3.7434 | 1.1702 | 1.7461 | 0 | 0.37353 | 0.84924 | 0.453 | 4.4672 | 3.664 | 8.4118 | 12.7373 | 8.803 | 4.6648 | 8.0718 | 10.839 | 6.1949 | 3.0641 | 0.18421
51 | 2.3366 | 14.5968 | 12.8354 | 18.6303 | 21.6748 | 14.493 | 12.2703 | 9.0014 | 5.3688 | 2.672 | 1.1417 | 1.9344 | 5.7045 | 9.3022 | 8.9824 | 11.3284 | 14.0789 | 8.8914 | 11.2734 | 13.3893 | 4.8653 | 17.0868 | 4.1634 | 23.6151
52 | 23.4568 | 23.6762 | 30.5526 | 29.748 | 23.522 | 9.211 | 1.0596 | 1.8836 | 12.9306 | 4.7809 | 1.9758 | 0 | 0 | 0.81714 | 11.4983 | 20.9117 | 8.4133 | 4.6613 | 0 | 9.7373 | 30.7042 | 10.2444 | 37.1184 | 43.1857
53 | 25.3642 | 31.2833 | 38.831 | 40.4959 | 44.2176 | 33.3341 | 27.6489 | 27.5165 | 15.3609 | 1.868 | 0 | 0 | 0.67805 | 4.7895 | 11.8829 | 18.3431 | 45.8685 | 34.9499 | 27.3838 | 4.4543 | 57.0374 | 59.3573 | 41.0556 | 28.395
54 | 16.1515 | 8.5742 | 5.6849 | 5.2368 | 3.1272 | 14.0448 | 39.6194 | 57.7882 | 55.7273 | 46.1204 | 29.9769 | 25.5748 | 16.873 | 8.6667 | 13.0593 | 25.6943 | 51.7583 | 29.4639 | 14.5419 | 59.3377 | 57.9809 | 59.4 | 58.6338 | 59.1549
55 | 59.4 | 59.4 | 59.3583 | 59.356 | 59.4 | 49.1346 | 7.2497 | 27.0119 | 4.9139 | 55.461 | 59.4 | 59.4 | 59.0757 | 58.0034 | 58.2788 | 59.1913 | 59.4 | 59.4 | 59.3198 | 59.12 | 58.5033 | 55.106 | 55.1833 | 57.2038
56 | 41.3146 | 43.736 | 54.9869 | 58.528 | 59.4 | 59.3937 | 54.1383 | 53.6095 | 42.5795 | 58.511 | 59.3309 | 54.4462 | 32.258 | 15.1973 | 7.5565 | 10.6395 | 12.6459 | 6.6935 | 8.3989 | 32.9078 | 59.1735 | 57.2583 | 57.9363 | 58.3855
57 | 48.7714 | 11.4281 | 12.8323 | 7.1399 | 5.4014 | 4.8484 | 3.3703 | 3.4835 | 4.3729 | 13.7314 | 12.9001 | 11.6488 | 11.5347 | 10.1616 | 11.779 | 18.9793 | 32.8511 | 28.0177 | 23.6948 | 16.7688 | 9.0877 | 6.5074 | 5.43 | 8.0836
58 | 10.0597 | 6.758 | 4.3393 | 2.5678 | 0.088211 | 0 | 3.3755 | 7.1866 | 7.246 | 7.4688 | 6.7616 | 6.7779 | 5.4798 | 6.1797 | 6.6688 | 9.8788 | 11.2956 | 10.7474 | 7.8149 | 6.9401 | 4.3388 | 3.8286 | 2.7648 | 1.0378
59 | 0.91801 | 0 | 0 | 2.4251 | 0.24086 | 4.1749 | 3.3362 | 3.6833 | 3.7565 | 9.1008 | 8.0417 | 7.4666 | 6.6489 | 9.9056 | 18.9482 | 5.782 | 13.2133 | 27.2499 | 17.3979 | 0 | 5.3838 | 57.3887 | 59.4 | 59.3063
60 | 58.7822 | 56.6378 | 49.4439 | 42.2777 | 53.6525 | 54.8003 | 46.9412 | 34.1651 | 17.0983 | 15.576 | 8.4749 | 2.7159 | 6.4021 | 7.9448 | 12.9671 | 19.9632 | 40.6816 | 46.4133 | 38.7002 | 40.4144 | 30.6048 | 54.6911 | 44.6394 | 26.4297
61 | 41.224 | 34.4248 | 16.2105 | 12.5963 | 12.31 | 9.6793 | 6.857 | 4.9172 | 8.4525 | 20.3427 | 31.6713 | 37.9951 | 35.7374 | 58.7465 | 59.4 | 59.2949 | 59.3253 | 59.2546 | 47.55 | 39.6748 | 34.4257 | 43.1414 | 57.6667 | 59.0185
62 | 55.481 | 38.6576 | 21.9802 | 10.5258 | 4.9682 | 10.3147 | 17.9467 | 13.1259 | 1.3532 | 1.7231 | 3.675 | 5.8432 | 6.8419 | 10.5533 | 13.7444 | 22.5807 | 29.8194 | 27.3814 | 0.091124 | 13.7793 | 11.6985 | 3.3813 | 0.24983 | 1.8276
63 | 38.3452 | 46.6456 | 0.48576 | 0 | 0 | 0.37406 | 0 | 0.10628 | 9.6711 | 23.2887 | 33.3631 | 0.75901 | 0.90559 | 12.0692 | 10.991 | 20.2126 | 44.8137 | 33.0074 | 0 | 7.758 | 13.7124 | 3.4171 | 4.6875 | 9.3125
64 | 11.1223 | 8.0457 | 5.5748 | 10.3799 | 32.7121 | 10.3849 | 14.477 | 17.1325 | 23.6243 | 15.9576 | 14.2444 | 8.5448 | 16.0847 | 1.9524 | 0 | 0 | 3.9057 | 30.5771 | 42.4252 | 49.5424 | 59.4 | 59.1905 | 59.4 | 59.2721
65 | 56.4279 | 53.804 | 41.8881 | 34.4787 | 38.6901 | 56.9538 | 59.3746 | 59.3643 | 58.8084 | 59.4 | 59.1595 | 58.1925 | 58.9725 | 39.8244 | 3.5898 | 4.2474 | 17.01 | 0.51345 | 3.1281 | 39.367 | 30.0242 | 29.1901 | 2.2415 | 19.7807
66 | 32.1801 | 15.8021 | 2.6768 | 4.2558 | 5.1159 | 9.1005 | 8.6732 | 15.7145 | 18.0315 | 19.07 | 5.3507 | 0 | 0 | 0 | 0 | 0 | 2.4926 | 8.1161 | 8.8779 | 5.4193 | 8.6068 | 11.3651 | 8.2842 | 7.95
67 | 6.9453 | 10.393 | 12.8389 | 12.0843 | 11.6855 | 9.4797 | 7.8499 | 5.4511 | 0.12994 | 1.0513 | 2.7174 | 2.9154 | 2.6554 | 3.6336 | 3.1425 | 0.66753 | 1.1567 | 3.7001 | 3.1238 | 0 | 0.10896 | 10.514 | 9.8995 | 8.5663
68 | 12.1943 | 14.2617 | 10.1276 | 8.3677 | 9.8307 | 13.4123 | 12.2056 | 7.8544 | 0.59019 | 0.215 | 2.8424 | 3.032 | 2.8771 | 5.3235 | 8.4886 | 8.1451 | 13.0642 | 11.9998 | 16.584 | 10.8868 | 42.5754 | 25.6339 | 19.6317 | 23.5722
69 | 43.3734 | 52.7208 | 19.0208 | 8.5741 | 7.2988 | 5.9997 | 4.7277 | 4.195 | 0.36818 | 0.072281 | 0 | 0 | 7.1852 | 24.3679 | 3.1443 | 4.9638 | 49.5964 | 53.8378 | 26.5942 | 2.0978 | 0.66004 | 4.1646 | 9.2159 | 11.4419
70 | 6.87 | 9.3287 | 5.8855 | 4.6225 | 4.9694 | 2.8609 | 0.23277 | 0 | 0 | 0 | 8.9869 | 19.5482 | 28.8234 | 58.7559 | 59.1543 | 59.4 | 59.0844 | 55.7018 | 39.7135 | 34.9937 | 31.682 | 52.1432 | 57.5544 | 42.3714
71 | 21.4243 | 14.7318 | 19.0471 | 58.3141 | 59.4 | 59.4 | 58.9724 | 44.9251 | 13.5857 | 11.1095 | 29.288 | 45.11 | 17.7518 | 9.3448 | 7.3813 | 6.9588 | 12.2213 | 20.3537 | 17.7462 | 32.6622 | 7.9754 | 20.9432 | 3.0187 | 8.1487
72 | 12.0073 | 0.29958 | 3.89 | 7.7378 | 7.5768 | 1.9681 | 0 | 0.36289 | 0 | 0.54579 | 7.0489 | 25.4973 | 33.0889 | 49.23 | 51.1824 | 49.4741 | 59.1444 | 49.0393 | 58.8798 | 59.4 | 58.7852 | 59.2699 | 31.2105 | 46.6129
73 | 54.5198 | 54.9382 | 59.3342 | 58.8863 | 56.7294 | 43.5644 | 33.851 | 33.1218 | 28.4824 | 48.491 | 25.6034 | 26.1982 | 53.4225 | 48.659 | 16.3248 | 4.4047 | 5.2099 | 40.8723 | 12.4011 | 11.4938 | 19.081 | 30.5998 | 40.8006 | 29.0427
74 | 7.4088 | 8.1286 | 5.1296 | 3.6113 | 3.8668 | 4.09 | 1.7846 | 0.81726 | 0.36128 | 1.1142 | 2.4077 | 3.0533 | 3.4927 | 4.9757 | 4.8501 | 3.4912 | 2.057 | 4.1265 | 0.62384 | 0 | 0 | 2.2447 | 3.657 | 5.8977
75 | 8.6984 | 5.5091 | 2.9154 | 4.8231 | 7.4747 | 7.762 | 8.6705 | 8.9833 | 11.3466 | 14.2398 | 12.2338 | 9.2131 | 10.6892 | 13.4044 | 11.5753 | 10.1541 | 3.1661 | 0 | 0 | 1.8461 | 8.7347 | 9.5817 | 13.3617 | 20.047
76 | 32.2927 | 27.3709 | 32.7294 | 35.0887 | 33.6678 | 28.3025 | 24.2116 | 20.2728 | 15.8106 | 7.5577 | 4.5359 | 1.3678 | 0.036081 | 0 | 0 | 0 | 0 | 4.5693 | 7.4193 | 18.2438 | 38.4531 | 29.3803 | 37.8989 | 50.1085
77 | 39.6875 | 43.554 | 53.3975 | 59.2857 | 59.4 | 59.1656 | 58.9299 | 59.0674 | 59.4 | 59.4 | 59.0521 | 59.3324 | 59.4 | 59.3855 | 56.7942 | 58.0908 | 42.1949 | 51.2925 | 45.91 | 49.9379 | 56.5141 | 57.5427 | 44.2766 | 19.0167
78 | 18.6417 | 13.252 | 11.6077 | 16.9381 | 17.1593 | 19.6551 | 14.6812 | 14.6415 | 25.3913 | 47.8899 | 58.6551 | 59.3334 | 59.4 | 59.4 | 59.4 | 59.3446 | 59.4 | 56.5185 | 40.5516 | 48.0432 | 30.455 | 29.3876 | 17.1933 | 16.2317
79 | 17.1992 | 12.7383 | 13.2342 | 18.5032 | 18.1636 | 8.5892 | 1.1542 | 0 | 0 | 1.9278 | 3.1361 | 6.3537 | 7.5743 | 19.0429 | 27.1619 | 10.6655 | 7.6196 | 2.6337 | 0 | 0.68072 | 5.1356 | 5.1098 | 0.45318 | 3.1728
80 | 18.8241 | 22.4351 | 30.3668 | 36.248 | 40.9054 | 36.7731 | 29.1895 | 22.626 | 10.7007 | 5.9419 | 5.2535 | 3.0427 | 0 | 0 | 0 | 0 | 0 | 9.8056 | 18.0831 | 58.2489 | 59.4 | 55.9665 | 48.0241 | 59.3062
81 | 0.26856 | 0.30808 | 1.4674 | 2.5085 | 6.4336 | 8.2653 | 9.4209 | 5.3244 | 1.8621 | 0.046721 | 0 | 2.4606 | 10.3611 | 22.408 | 18.4384 | 17.6274 | 0.12952 | 13.4557 | 26.4634 | 39.5131 | 59.4 | 59.4 | 59.3657 | 59.4
82 | 59.1211 | 57.8055 | 54.3239 | 55.9706 | 56.0179 | 55.8509 | 56.7437 | 57.1622 | 57.9379 | 58.6996 | 52.0555 | 8.5298 | 18.4526 | 59.4 | 57.5998 | 36.9469 | 53.282 | 59.4 | 59.3177 | 58.9776 | 59.2234 | 50.9337 | 57.9703 | 40.1166
83 | 16.9568 | 45.6313 | 26.6325 | 55.758 | 52.9976 | 49.4603 | 56.5744 | 54.6274 | 47.8044 | 53.0457 | 52.639 | 56.7019 | 57.1481 | 59.0427 | 59.4 | 59.4 | 59.4 | 55.2353 | 43.6759 | 29.2138 | 12.8348 | 1.5665 | 1.8246 | 4.6463
84 | 0 | 0 | 0 | 0 | 1.2314 | 4.6645 | 9.6193 | 13.0677 | 11.144 | 9.7032 | 6.8485 | 10.9665 | 15.0484 | 22.0786 | 28.3021 | 41.9396 | 56.897 | 49.206 | 26.7089 | 3.515 | 7.8475 | 15.6949 | 36.273 | 41.8001
85 | 59.4 | 50.0007 | 28.0528 | 48.1087 | 45.1001 | 57.5359 | 28.634 | 41.8688 | 58.6969 | 59.4 | 59.4 | 59.3821 | 28.5111 | 53.2276 | 14.9883 | 26.3361 | 3.5759 | 0.58146 | 1.5443 | 0.89453 | 3.3307 | 3.7779 | 3.977 | 3.7953
86 | 7.9979 | 11.0468 | 11.6963 | 17.3966 | 25.5423 | 31.562 | 29.8776 | 26.709 | 27.5156 | 15.9725 | 4.3162 | 5.5477 | 8.8204 | 11.3646 | 15.2997 | 49.4066 | 55.0557 | 22.9657 | 38.6063 | 30.2198 | 40.5257 | 51.6525 | 42.5084 | 27.8353
87 | 35.1999 | 37.8225 | 3.6512 | 8.4908 | 3.4875 | 6.3186 | 4.9388 | 0.11127 | 1.2305 | 5.4753 | 7.1285 | 17.5761 | 31.8296 | 40.4441 | 57.2698 | 57.4338 | 44.8284 | 59.1866 | 54.0272 | 54.4151 | 49.0037 | 51.717 | 13.9974 | 32.5629
88 | 24.3168 | 12.6787 | 12.0792 | 31.2054 | 17.3747 | 34.9791 | 38.8927 | 53.0678 | 56.6434 | 59.4 | 59.388 | 59.3031 | 59.4 | 59.4 | 59.4 | 58.9191 | 49.1936 | 25.2428 | 6.4903 | 2.0775 | 0 | 0.066931 | 12.1577 | 26.1825
89 | 34.4691 | 28.6911 | 14.6631 | 15.3588 | 36.5208 | 56.4107 | 57.5035 | 47.5338 | 38.5699 | 21.847 | 6.3058 | 4.1743 | 8.2498 | 27.2651 | 33.0096 | 26.0557 | 32.2169 | 27.5746 | 29.0648 | 59.3636 | 58.2608 | 57.9515 | 55.9826 | 32.2892
90 | 9.2447 | 1.1684 | 0.24216 | 2.5471 | 6.1865 | 4.1004 | 1.7028 | 0.12191 | 0.99422 | 21.434 | 47.4292 | 59.4 | 59.0617 | 59.4 | 58.7868 | 59.1434 | 57.512 | 58.9755 | 58.7389 | 14.4002 | 0 | 11.0842 | 7.457 | 18.8463
91 | 42.2754 | 43.7429 | 37.6762 | 25.2897 | 24.8365 | 21.7812 | 18.1736 | 13.8504 | 4.4064 | 16.4041 | 56.1165 | 36.8902 | 30.1708 | 29.1285 | 35.062 | 24.8451 | 46.0701 | 40.739 | 37.0947 | 36.2719 | 12.0308 | 13.684 | 59.2565 | 46.7847
92 | 13.7883 | 50.3519 | 19.4556 | 14.8596 | 5.8636 | 13.0802 | 5.307 | 3.3228 | 4.6247 | 3.1682 | 2.7306 | 1.809 | 0.99867 | 0 | 1.1839 | 2.1181 | 2.1327 | 5.2085 | 2.8099 | 5.906 | 12.2557 | 18.0948 | 24.9078 | 28.4394
93 | 28.1715 | 25.1283 | 24.3911 | 7.1211 | 3.3219 | 9.7651 | 5.4659 | 0.35308 | 0 | 0 | 2.0567 | 16.1665 | 29.211 | 45.9958 | 50.1668 | 57.8399 | 57.6725 | 58.1112 | 59.4 | 36.1341 | 37.9488 | 33.6291 | 42.9126 | 54.052
94 | 48.8172 | 46.0779 | 20.313 | 9.6191 | 17.4094 | 28.1658 | 45.9919 | 58.9403 | 59.3687 | 59.4 | 59.4 | 58.5293 | 59.3496 | 59.4 | 59.4 | 59.4 | 58.1814 | 59.2468 | 50.4274 | 59.0865 | 59.4 | 58.9407 | 56.4633 | 50.4393
95 | 45.1898 | 49.4312 | 47.4814 | 45.1174 | 35.2697 | 36.4334 | 38.9049 | 39.6002 | 43.8833 | 37.0977 | 29.0573 | 16.6245 | 11.7815 | 14.6232 | 47.6114 | 55.1893 | 38.9905 | 23.2847 | 32.5188 | 14.5853 | 12.5425 | 12.3327 | 14.4353 | 8.2529
96 | 4.4559 | 0.72637 | 0 | 0 | 0 | 0 | 0.071092 | 0 | 1.7805 | 3.6965 | 6.0681 | 8.6916 | 10.8525 | 11.4849 | 13.6723 | 12.5434 | 13.0639 | 17.7362 | 11.753 | 10.603 | 14.713 | 7.8608 | 4.8653 | 0
97 | 0 | 0 | 0 | 0 | 0 | 0.074718 | 0.5024 | 0 | 2.6524 | 3.7519 | 5.2324 | 4.6235 | 4.6231 | 3.8986 | 5.3332 | 7.0628 | 6.6731 | 8.4293 | 11.7922 | 12.7093 | 10.9211 | 19.5605 | 25.3251 | 22.9223
98 | 58.5895 | 57.4725 | 57.5444 | 57.5068 | 57.8177 | 58.1198 | 58.5913 | 50.5276 | 54.9864 | 53.7842 | 32.4329 | 6.9812 | 9.7269 | 19.1299 | 26.7583 | 37.8909 | 35.2826 | 33.2715 | 56.2435 | 59.4 | 59.3779 | 58.9185 | 59.4 | 59.2062
99 | 50.6992 | 51.4334 | 58.2595 | 58.8555 | 58.6317 | 59.0018 | 58.3253 | 53.2459 | 59.1498 | 58.5051 | 59.4 | 59.4 | 58.7874 | 57.7008 | 53.6637 | 54.6381 | 57.7707 | 57.3837 | 56.8254 | 58.7 | 59.3628 | 58.6485 | 55.8197 | 58.5959
100 | 58.897 | 58.8053 | 59.4 | 51.3128 | 58.0603 | 37.2239 | 51.8044 | 43.2742 | 53.4045 | 59.4 | 59.3714 | 59.4 | 59.4 | 59.4 | 59.3561 | 58.9007 | 50.6504 | 57.258 | 57.504 | 58.4071 | 59.4 | 8.8112 | 31.7132 | 4.4876
101 | 5.2744 | 5.5242 | 7.1384 | 8.7851 | 8.3434 | 7.6199 | 8.2399 | 4.0938 | 0.21339 | 0 | 2.2612 | 4.7828 | 5.6887 | 6.0494 | 10.7609 | 15.1855 | 28.4346 | 37.5925 | 30.6732 | 33.2827 | 59.4 | 50.0649 | 23.1556 | 55.9906
102 | 55.5419 | 58.6707 | 58.8747 | 59.2074 | 58.3925 | 59.1002 | 58.573 | 55.913 | 59.3819 | 59.3038 | 57.3608 | 42.7564 | 30.286 | 11.4806 | 8.716 | 10.2454 | 23.1413 | 59.4 | 59.4 | 59.4 | 59.3426 | 57.8855 | 45.9923 | 30.4011
103 | 17.1063 | 13.7045 | 12.3592 | 22.0258 | 15.0677 | 11.6492 | 2.3778 | 1.0194 | 9.5661 | 9.9748 | 13.076 | 22.7968 | 34.987 | 23.1955 | 27.6583 | 28.1275 | 50.5157 | 41.5349 | 43.2167 | 31.5403 | 14.9261 | 2.5691 | 5.1492 | 0.12031
104 | 0 | 0.12174 | 0.20668 | 0.37971 | 0 | 0 | 0 | 3.9838 | 12.7033 | 6.1779 | 23.8078 | 57.8261 | 0 | 0 | 0 | 51.4928 | 54.7623 | 42.0497 | 52.076 | 54.2506 | 57.5885 | 59.2175 | 59.4 | 59.4
105 | 59.3973 | 59.4 | 52.2828 | 26.73 | 26.1912 | 45.6748 | 8.1299 | 11.6729 | 6.4069 | 1.0714 | 0 | 0.668 | 4.7876 | 7.4481 | 14.1765 | 25.1456 | 56.7392 | 59.1597 | 58.8234 | 59.4 | 47.9877 | 53.953 | 25.8156 | 50.707
106 | 46.2027 | 57.726 | 55.9238 | 59.0862 | 59.4 | 59.4 | 59.4 | 59.395 | 26.7769 | 59.2038 | 27.043 | 31.1535 | 9.9731 | 22.1282 | 13.5866 | 23.1012 | 17.389 | 26.6551 | 25.9388 | 37.7766 | 23.8035 | 26.3532 | 32.978 | 27.5595
107 | 7.35 | 11.8032 | 23.2096 | 32.8782 | 22.6154 | 11.6436 | 30.574 | 30.8857 | 25.9 | 23.651 | 10.9158 | 7.7073 | 7.5379 | 4.8543 | 3.6969 | 5.3056 | 5.8427 | 12.0327 | 10.6861 | 9.5629 | 10.4638 | 11.2653 | 10.1074 | 7.2178
108 | 4.3193 | 0.083218 | 0 | 1.4463 | 0 | 0 | 1.016 | 0.59257 | 3.9994 | 6.7009 | 8.1453 | 5.6981 | 2.985 | 2.1417 | 3.8173 | 3.1089 | 18.576 | 8.3389 | 0 | 0.033763 | 0 | 0 | 0 | 0
109 | 0 | 0 | 0 | 0 | 0 | 0.44825 | 2.6881 | 0.80406 | 2.0126 | 3.8529 | 2.6618 | 1.9461 | 1.7811 | 4.5293 | 13.1097 | 16.173 | 2.2447 | 0.14099 | 0.40325 | 0 | 0 | 3.2829 | 7.1324 | 35.2836
110 | 58.2617 | 57.0676 | 29.4848 | 14.3501 | 7.1512 | 5.68 | 5.1529 | 0.14325 | 0.49966 | 2.2437 | 2.8182 | 3.5803 | 3.323 | 3.0993 | 6.4144 | 8.3582 | 8.9396 | 3.205 | 3.914 | 14.2644 | 8.6343 | 9.9545 | 13.5042 | 9.9198
111 | 3.973 | 4.0849 | 5.7416 | 7.0981 | 12.9569 | 17.7178 | 13.8097 | 5.4615 | 1.0822 | 0 | 0.058015 | 0.60173 | 0.72768 | 0.11817 | 0.58835 | 2.3905 | 1.9529 | 4.019 | 21.7076 | 19.3656 | 17.9421 | 15.5156 | 19.8805 | 25.9907
112 | 18.5074 | 10.3331 | 2.823 | 3.4757 | 3.8522 | 4.9481 | 4.4305 | 9.9531 | 9.361 | 7.1802 | 11.7931 | 18.3712 | 29.8822 | 2.0659 | 23.9287 | 9.3265 | 19.3704 | 1.8797 | 14.46 | 24.6052 | 24.0231 | 41.2263 | 34.8393 | 13.4154
113 | 10.2198 | 44.0662 | 24.8467 | 9.6589 | 6.3415 | 2.6331 | 9.5844 | 7.9905 | 4.193 | 0.64648 | 0 | 0 | 0 | 2.5834 | 7.4913 | 5.5383 | 7.8701 | 8.497 | 6.2037 | 10.4107 | 23.9006 | 38.1624 | 58.677 | 59.4
114 | 59.2481 | 58.9988 | 56.5176 | 57.7326 | 58.6858 | 59.3201 | 59.4 | 58.8592 | 58.2831 | 59.4 | 59.4 | 59.4 | 59.3142 | 44.0206 | 59.4 | 59.0045 | 58.1334 | 56.8077 | 57.8246 | 57.5668 | 56.6936 | 57.9775 | 56.8326 | 57.171
115 | 59.2638 | 56.1675 | 7.8342 | 13.262 | 0 | 2.1156 | 12.34 | 8.2303 | 4.1075 | 3.6529 | 0.82754 | 0.52927 | 0.029186 | 0 | 0 | 1.8153 | 42.0051 | 24.8208 | 7.5614 | 2.1495 | 43.8324 | 43.4287 | 33.2624 | 16.3993
116 | 5.3821 | 0.98702 | 0 | 0.34203 | 0.41906 | 1.3591 | 0.57272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5151 | 59.397 | 59.1367 | 59.4 | 57.5641 | 57.9851 | 59.0749 | 42.3724 | 5.3874
117 | 7.2129 | 9.6472 | 9.4446 | 2.9404 | 6.7772 | 3.8295 | 1.4859 | 2.7189 | 0 | 0 | 1.3727 | 9.5312 | 11.8244 | 16.1684 | 4.6792 | 0.73101 | 9.8646 | 10.3718 | 35.5429 | 58.9142 | 58.8215 | 59.3397 | 56.7368 | 45.003
118 | 58.0477 | 52.7514 | 41.648 | 31.2937 | 42.1548 | 49.7475 | 49.6118 | 56.3327 | 58.4908 | 59.4 | 59.4 | 59.4 | 59.4 | 59.4 | 59.4 | 59.4 | 59.4 | 59.3551 | 51.2964 | 45.7082 | 58.8968 | 57.1417 | 30.3825 | 19.5563
119 | 16.2109 | 22.7515 | 25.5947 | 24.0572 | 9.1407 | 3.1396 | 0 | 0 | 0 | 0.037983 | 0.036378 | 1.7344 | 0 | 0 | 0 | 1.038 | 18.5367 | 22.3225 | 15.1734 | 8.3551 | 0.72661 | 5.9531 | 41.5643 | 33.5313
120 | 30.1147 | 31.9251 | 24.0719 | 21.0529 | 21.6075 | 37.0413 | 49.0226 | 47.2841 | 58.7789 | 58.7732 | 28.8999 | 5.9976 | 1.1054 | 5.1307 | 22.564 | 31.9876 | 59.1822 | 58.6455 | 43.3377 | 11.4414 | 0.56927 | 0 | 0.22142 | 0.8833
121 | 8.0548 | 3.0685 | 1.9645 | 2.7647 | 4.0721 | 6.5513 | 7.5608 | 8.1007 | 11.476 | 17.7779 | 23.4067 | 31.0277 | 41.1317 | 45.5927 | 57.7421 | 56.1838 | 51.3281 | 38.3062 | 18.3674 | 4.836 | 0.84936 | 5.4078 | 6.386 | 3.2378
122 | 0.79705 | 0 | 0 | 0 | 1.6846 | 3.3884 | 4.4809 | 8.3877 | 11.1991 | 10.3861 | 14.383 | 22.3994 | 26.1839 | 31.3839 | 44.2141 | 56.6356 | 59.1078 | 47.3779 | 11.9103 | 15.4713 | 14.015 | 16.6562 | 13.6638 | 5.8052
123 | 2.0094 | 0.41912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5141 | 5.613 | 8.8128 | 14.0884 | 25.2055 | 21.2479 | 30.0793 | 55.0916 | 42.7162 | 51.3203 | 39.2267 | 33.266 | 45.2718 | 38.4926 | 21.3763
124 | 14.456 | 16.3499 | 15.5396 | 9.8854 | 10.4944 | 19.2223 | 10.5724 | 3.1799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5115 | 43.214 | 30.9878 | 8.9325 | 59.4 | 18.0898 | 43.0676 | 46.0679 | 32.1254
125 | 22.6622 | 24.5626 | 20.2747 | 27.4239 | 32.3737 | 38.0387 | 37.6317 | 21.8825 | 23.6837 | 16.6587 | 7.0499 | 3.4959 | 3.1432 | 1.2338 | 6.9006 | 8.5936 | 59.1374 | 36.2122 | 48.2917 | 59.3416 | 59.4 | 59.3324 | 59.3754 | 59.3445
126 | 26.7395 | 25.0583 | 50.7482 | 55.2692 | 55.2145 | 56.5489 | 55.4316 | 35.5725 | 15.5497 | 4.6338 | 0 | 54.8082 | 59.4 | 59.4 | 58.1911 | 58.5832 | 58.6295 | 55.1841 | 57.7336 | 59.1805 | 56.8332 | 59.2011 | 59.4 | 59.4
127 | 47.5531 | 58.8908 | 57.8978 | 58.9096 | 57.2176 | 50.971 | 52.6248 | 59.0275 | 59.4 | 59.3184 | 59.4 | 59.4 | 51.7761 | 23.9762 | 30.2323 | 49.0334 | 59.372 | 59.4 | 58.3159 | 57.5986 | 59.4 | 59.3987 | 59.3992 | 59.4
128 | 25.6963 | 4.1471 | 10.5834 | 50.2817 | 51.8319 | 56.7244 | 57.6014 | 59.0718 | 58.6493 | 59.2422 | 58.4084 | 36.7668 | 31.756 | 53.9167 | 57.7861 | 52.8046 | 56.5579 | 59.4 | 59.4 | 59.2922 | 59.4 | 59.4 | 59.2613 | 59.4
129 | 58.9868 | 59.4 | 59.4 | 39.9989 | 59.3079 | 59.4 | 59.4 | 52.3801 | 40.1279 | 58.4393 | 45.3631 | 19.3843 | 2.2466 | 0.26547 | 1.2008 | 1.9864 | 0 | 0.47196 | 0 | 4.4596 | 15.2587 | 23.0295 | 13.9222 | 58.4929
130 | 59.4 | 59.4 | 59.4 | 57.8118 | 57.8053 | 59.4 | 59.4 | 59.2911 | 58.834 | 58.6698 | 59.0083 | 59.4 | 54.9444 | 45.7684 | 39.0552 | 50.506 | 59.1094 | 59.4 | 59.4 | 59.4 | 59.2068 | 7.218 | 8.228 | 20.4068
131 | 19.2666 | 10.6891 | 25.1521 | 12.6857 | 4.4878 | 2.9773 | 11.7285 | 6.3467 | 7.6417 | 6.3886 | 13.532 | 39.7907 | 42.9274 | 56.7122 | 35.9738 | 38.0516 | 14.6796 | 21.5136 | 6.4197 | 0 | 0 | 1.4457 | 2.0001 | 0.97086
132 | 0.033287 | 1.1114 | 2.3476 | 6.65 | 8.1365 | 6.9134 | 3.5367 | 0 | 0 | 0 | 0 | 0.18118 | 0.061819 | 0.1933 | 1.3929 | 5.1626 | 12.1006 | 13.5191 | 31.1158 | 59.2828 | 56.5091 | 38.9326 | 52.5907 | 47.5988
133 | 39.5194 | 49.1612 | 58.3456 | 58.5015 | 58.8327 | 54.5023 | 33.1017 | 13.5174 | 3.0209 | 0.48986 | 3.9145 | 3.662 | 0.27022 | 0 | 0 | 4.0776 | 12.6802 | 20.7128 | 59.1274 | 59.4 | 59.2411 | 46.369 | 31.8033 | 21.5416
134 | 36.9189 | 36.2895 | 34.0629 | 33.9485 | 21.3962 | 28.7089 | 19.4427 | 18.4381 | 15.1572 | 9.1277 | 5.8206 | 8.6096 | 8.4721 | 11.5193 | 9.6564 | 28.6235 | 51.4988 | 58.6915 | 36.5899 | 38.9423 | 0.032514 | 21.1668 | 13.7811 | 8.1125
135 | 12.6977 | 0 | 0 | 0 | 3.6404 | 5.2136 | 7.523 | 8.5238 | 11.0063 | 19.5059 | 28.4101 | 45.8052 | 35.2244 | 58.4623 | 59.2485 | 50.4555 | 59.3767 | 59.4 | 59.4 | 35.2851 | 51.6078 | 57.7899 | 16.9453 | 0
136 | 0 | 2.0283 | 6.5828 | 5.5786 | 4.638 | 13.9664 | 22.0751 | 22.7479 | 30.471 | 56.7993 | 59.4 | 59.4 | 59.4 | 59.4 | 54.112 | 47.3444 | 52.233 | 38.2591 | 24.4984 | 11.446 | 11.3346 | 12.1475 | 8.3208 | 15.5546
137 | 11.7088 | 7.3704 | 40.992 | 38.9464 | 23.6809 | 35.3715 | 7.8814 | 3.8078 | 18.7577 | 24.1192 | 29.7145 | 16.8287 | 15.4668 | 14.9689 | 10.5133 | 7.1576 | 6.7908 | 3.7787 | 4.0982 | 1.8569 | 1.1986 | 1.8886 | 2.8802 | 8.1179
138 | 11.3068 | 15.2691 | 14.1119 | 3.4987 | 0.66592 | 0.34916 | 1.5739 | 0.091361 | 0 | 0 | 0 | 0.25441 | 0.075788 | 0 | 2.4457 | 3.151 | 5.9773 | 9.5598 | 20.1178 | 10.7142 | 9.2947 | 8.7661 | 5.98 | 5.6574
139 | 3.6337 | 1.2113 | 0.17416 | 0.29311 | 0.53598 | 2.1378 | 1.8177 | 0 | 4.3074 | 12.258 | 18.7432 | 19.515 | 12.4939 | 13.2281 | 16.264 | 19.5013 | 28.9807 | 48.4738 | 38.1822 | 59.351 | 46.0922 | 0.15918 | 0.09683 | 5.5335
140 | 4.58 | 2.314 | 15.3615 | 15.1035 | 15.3309 | 16.0088 | 9.2891 | 0.60494 | 0 | 0 | 5.256 | 7.6877 | 2.0885 | 57.1905 | 58.3084 | 13.8784 | 40.7365 | 57.4749 | 8.7979 | 16.3438 | 1.0507 | 8.8979 | 4.5419 | 9.1225
141 | 6.8784 | 10.3448 | 9.6101 | 25.5714 | 22.1881 | 59.3866 | 47.795 | 42.5524 | 28.825 | 49.9131 | 53.6778 | 56.9781 | 36.0167 | 42.7705 | 47.2637 | 48.5392 | 55.2113 | 58.7774 | 59.2197 | 59.2465 | 59.1266 | 58.4736 | 55.899 | 57.4744
142 | 59.2061 | 58.5816 | 57.9499 | 54.5638 | 51.3849 | 57.0301 | 58.3952 | 59.2601 | 57.5397 | 16.1575 | 3.9064 | 0.49176 | 0.51191 | 0 | 1.7717 | 10.0494 | 52.5187 | 59.4 | 58.8425 | 58.7349 | 58.9578 | 59.4 | 57.5768 | 48.647
143 | 32.7272 | 12.8452 | 4.6984 | 7.4994 | 7.1239 | 3.4213 | 6.3648 | 9.0066 | 5.7894 | 10.4551 | 29.2462 | 49.034 | 49.7642 | 56.1262 | 58.5062 | 51.66 | 53.2738 | 14.0014 | 11.6976 | 0.7681 | 32.7476 | 38.7276 | 49.838 | 42.1058
144 | 35.2827 | 25.1181 | 22.7627 | 18.4956 | 11.3796 | 7.7148 | 7.7806 | 2.0828 | 1.3981 | 3.5553 | 7.3519 | 6.5566 | 10.931 | 24.7576 | 24.0561 | 45.2542 | 25.9745 | 3.2097 | 12.4392 | 7.8596 | 4.7737 | 18.5574 | 2.0854 | 1.3216
145 | 0.27325 | 4.8689 | 0.034417 | 4.0025 | 6.7783 | 7.2284 | 0.37698 | 0.27177 | 0 | 1.5246 | 2.6687 | 9.7712 | 9.7126 | 14.7539 | 14.7276 | 16.7455 | 20.5354 | 34.4994 | 19.8493 | 10.2227 | 1.868 | 2.6758 | 4.2046 | 7.4371
146 | 13.6378 | 7.9995 | 6.5257 | 2.5657 | 1.7629 | 2.5661 | 2.3854 | 12.8515 | 16.5889 | 28.9877 | 36.8258 | 56.6508 | 58.8515 | 58.8734 | 59.2683 | 58.8998 | 59.3327 | 59.2976 | 55.5296 | 29.4406 | 14.158 | 14.5551 | 14.4756 | 10.2349
147 | 2.1158 | 7.4132 | 11.9846 | 20.6242 | 20.1569 | 10.6662 | 6.0167 | 7.763 | 12.4924 | 17.0708 | 19.1528 | 17.0297 | 15.077 | 13.6918 | 13.1337 | 11.4136 | 9.2953 | 8.8402 | 4.3642 | 0.9828 | 0.99772 | 2.7218 | 3.5189 | 2.328
148 | 1.5455 | 0.9019 | 3.2762 | 4.9136 | 8.3855 | 10.8328 | 6.5875 | 6.3388 | 12.3564 | 25.9603 | 24.5058 | 18.9059 | 17.3113 | 26.8543 | 40.7129 | 9.5591 | 19.6487 | 30.2656 | 4.4149 | 16.1759 | 0.052606 | 0 | 14.1434 | 22.4252
149 | 14.0286 | 5.7633 | 2.6215 | 3.8029 | 8.6364 | 5.5528 | 6.4612 | 6.8713 | 6.5095 | 8.8574 | 8.7144 | 8.4772 | 0 | 0 | 0 | 1.2525 | 3.3304 | 9.7657 | 40.9679 | 22.8138 | 18.6226 | 18.9354 | 6.7033 | 0
150 | 0.75491 | 3.6573 | 1.5111 | 1.68 | 0.2046 | 0 | 0 | 0 | 0 | 5.4231 | 9.2859 | 2.0356 | 2.1986 | 6.0184 | 12.4892 | 10.2057 | 26.1221 | 40.8537 | 3.1518 | 4.3993 | 19.7342 | 9.4346 | 3.223 | 13.1037
151 | 24.0802 | 11.0994 | 4.5951 | 6.2789 | 8.8651 | 13.0854 | 7.129 | 4.4304 | 0.59643 | 1.4881 | 3.8927 | 5.8925 | 34.1372 | 0.70706 | 0.41258 | 1.9909 | 0.87355 | 4.5404 | 11.922 | 51.5076 | 46.1344 | 37.9287 | 12.279 | 0
152 | 28.8461 | 32.2711 | 51.3078 | 50.8024 | 43.8369 | 38.7632 | 33.0303 | 38.7422 | 59.4 | 59.3394 | 59.4 | 59.4 | 59.0472 | 59.4 | 59.4 | 59.3471 | 59.1277 | 38.2646 | 51.7829 | 45.6159 | 28.5204 | 14.1227 | 16.8688 | 29.5723
153 | 36.7499 | 23.6806 | 17.4079 | 11.1456 | 5.7853 | 1.8742 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1317 | 8.6964 | 23.1745 | 28.5968 | 45.4758 | 59.318 | 58.9807 | 59.2995 | 59.4 | 59.3273 | 59.1251 | 59.3695
154 | 59.3814 | 59.4 | 59.4 | 58.4512 | 52.5492 | 14.6228 | 9.6162 | 17.5947 | 58.496 | 59.4 | 59.4 | 59.4 | 59.4 | 59.4 | 58.4268 | 58.2898 | 58.5255 | 59.3625 | 59.4 | 59.3944 | 59.3991 | 59.4 | 39.5084 | 0.68173
155 | 1.2847 | 6.5661 | 5.4965 | 9.8131 | 13.6057 | 8.2178 | 0.56969 | 0.85233 | 2.5215 | 4.1599 | 17.256 | 23.0067 | 24.3137 | 35.6648 | 59.4 | 29.3513 | 58.5124 | 58.7564 | 46.2974 | 26.2406 | 8.6745 | 0 | 7.5482 | 5.4074
156 | 20.0906 | 3.9067 | 0.4514 | 1.0946 | 6.8075 | 2.5821 | 3.544 | 0 | 0 | 2.2165 | 7.456 | 18.7102 | 17.6921 | 36.7456 | 54.1995 | 53.0648 | 57.982 | 58.2987 | 25.6696 | 33.088 | 17.3131 | 15.3239 | 17.5177 | 17.7156
157 | 2.4458 | 0.085833 | 0.634 | 0.93287 | 6.2657 | 0 | 0.46346 | 3.1529 | 9.1839 | 35.0455 | 44.1491 | 57.9949 | 34.836 | 52.7537 | 34.7963 | 59.0831 | 48.1957 | 35.1089 | 0.16216 | 0 | 4.9625 | 9.2935 | 2.6015 | 0.15508
158 | 4.4173 | 22.6665 | 26.4172 | 2.9464 | 9.8071 | 3.3542 | 0 | 0 | 0 | 3.6375 | 6.4764 | 14.3632 | 32.9657 | 37.0945 | 49.2524 | 59.2561 | 41.8979 | 58.6187 | 48.2398 | 42.4833 | 22.9138 | 5.6514 | 37.8404 | 3.5572
159 | 59.3114 | 59.4 | 59.3624 | 59.3507 | 56.1538 | 22.2928 | 26.5342 | 9.8273 | 11.617 | 5.5982 | 32.5832 | 3.8026 | 45.8959 | 39.9092 | 20.2293 | 0.029007 | 2.2741 | 40.3784 | 57.8152 | 57.4238 | 48.1562 | 44.7754 | 28.7206 | 59.2785
160 | 46.4904 | 42.5749 | 23.324 | 20.954 | 16.7025 | 10.1557 | 2.3379 | 0 | 0 | 0 | 9.1647 | 45.9503 | 55.8213 | 4.895 | 33.568 | 31.334 | 27.716 | 4.8063 | 34.8866 | 59.1612 | 57.5517 | 23.0714 | 59.2535 | 54.586
161 | 58.848 | 59.4 | 59.3876 | 29.8064 | 28.3286 | 16.7689 | 26.466 | 45.4687 | 59.3715 | 55.2452 | 59.4 | 59.1565 | 34.1336 | 23.8827 | 25.0296 | 28.1132 | 29.5838 | 35.2641 | 4.9843 | 0 | 7.3946 | 12.9339 | 21.4759 | 22.6177
162 | 19.5679 | 11.6534 | 7.3001 | 4.9201 | 3.8602 | 5.8853 | 3.0002 | 4.2461 | 7.8541 | 14.4302 | 15.9248 | 7.4932 | 1.6919 | 0 | 0 | 0 | 0 | 6.5957 | 11.8196 | 11.098 | 17.4648 | 41.9981 | 54.9811 | 55.2708
163 | 36.6586 | 10.3144 | 18.3356 | 18.2212 | 11.8946 | 7.7606 | 5.9378 | 2.9025 | 4.911 | 0.029007 | 2.9491 | 14.1243 | 6.7662 | 4.1546 | 0.32033 | 4.0143 | 17.0005 | 35.1852 | 47.2554 | 51.8595 | 48.1805 | 55.1034 | 56.0626 | 34.5618
164 | 15.2421 | 23.6228 | 36.8664 | 49.8277 | 59.1873 | 59.4 | 51.8492 | 34.9046 | 31.9863 | 42.9162 | 46.9357 | 58.6148 | 44.2623 | 24.9644 | 26.0712 | 53.0278 | 16.358 | 8.7798 | 4.7086 | 0 | 6.0504 | 35.1941 | 47.0896 | 32.8728
165 | 15.4008 | 17.1232 | 8.4726 | 8.0958 | 6.1943 | 3.7544 | 1.0663 | 0 | 0 | 1.8134 | 14.0175 | 27.276 | 46.3356 | 23.5604 | 58.6404 | 57.4737 | 58.8571 | 58.0172 | 58.8425 | 55.1687 | 57.4232 | 58.4306 | 39.5337 | 3.8679
166 | 18.5519 | 10.4534 | 8.5657 | 13.1946 | 14.6651 | 31.003 | 16.9653 | 39.3414 | 50.3401 | 56.0415 | 48.3193 | 19.1863 | 0.93959 | 0 | 3.3577 | 6.7887 | 7.1554 | 46.2755 | 50.3749 | 55.5131 | 3.1042 | 38.6691 | 18.5635 | 25.764
167 | 43.0128 | 41.3481 | 28.5102 | 23.0916 | 22.3625 | 11.8315 | 17.0144 | 14.0338 | 12.2195 | 19.0575 | 44.0644 | 0 | 30.1452 | 59.4 | 13.8435 | 13.2903 | 52.51 | 20.3384 | 14.829 | 3.4645 | 6.4191 | 0.14337 | 0 | 0
168 | 7.0329 | 22.0746 | 13.8317 | 17.4163 | 4.7592 | 3.3419 | 26.6947 | 18.7352 | 11.8627 | 9.3689 | 11.2498 | 8.7966 | 4.0507 | 1.006 | 0 | 3.9561 | 39.9185 | 23.2339 | 0 | 2.659 | 15.6514 | 18.667 | 19.5762 | 28.4269
169 | 8.9526 | 2.7734 | 3.7207 | 4.3429 | 0 | 23.9281 | 27.7548 | 8.6392 | 17.3339 | 0 | 0 | 3.5949 | 6.2607 | 4.4371 | 8.9702 | 12.739 | 18.6361 | 25.5178 | 45.011 | 11.9264 | 28.4827 | 2.4023 | 11.4872 | 5.4044
170 | 0.25328 | 0.18641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27361 | 2.9341 | 6.9307 | 4.667 | 7.9547 | 5.5221 | 36.4842 | 54.2675 | 0 | 21.911 | 40.9897 | 57.0126 | 59.3953 | 58.429 | 59.353
171 | 58.9711 | 59.1719 | 59.3849 | 59.4 | 58.2099 | 54.3453 | 33.0256 | 21.3411 | 14.1438 | 7.0949 | 0 | 0 | 49.9754 | 45.5353 | 45.4374 | 20.2274 | 0.44664 | 56.2213 | 58.6829 | 56.9737 | 59.4 | 59.0566 | 59.3408 | 57.8803
172 | 57.505 | 55.3397 | 39.2945 | 33.1261 | 13.3807 | 28.3484 | 19.0041 | 18.1872 | 19.5693 | 16.2759 | 6.1828 | 20.3353 | 21.9566 | 56.4014 | 56.3609 | 58.96 | 35.4879 | 15.1133 | 0.12215 | 46.8544 | 46.6821 | 18.6433 | 37.1344 | 20.7515
173 | 5.3064 | 0.60184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5255 | 3.1984 | 3.9688 | 4.2302 | 2.868 | 4.9303 | 8.6947 | 8.3926 | 12.8996 | 18.2282 | 22.4724 | 19.7356 | 33.6929 | 44.1939 | 22.3393
174 | 9.2701 | 15.3123 | 24.9035 | 16.0967 | 13.3266 | 9.114 | 1.8392 | 0 | 0 | 0.56232 | 4.2105 | 6.743 | 1.633 | 3.2611 | 56.9173 | 10.7147 | 20.6513 | 26.2726 | 44.8954 | 16.6057 | 50.3856 | 57.5556 | 44.6449 | 58.4774
175 | 25.9156 | 2.6414 | 4.4474 | 11.0057 | 11.8902 | 10.6116 | 9.6022 | 6.7351 | 13.9274 | 16.3294 | 10.4406 | 14.4863 | 16.0601 | 1.4642 | 57.483 | 0.46186 | 0 | 41.6416 | 59.4 | 16.2956 | 25.4139 | 58.7187 | 2.4856 | 14.3127
176 | 12.9825 | 12.8809 | 13.3392 | 7.543 | 0 | 1.6957 | 1.362 | 2.5743 | 5.0715 | 13.3964 | 14.4812 | 22.3472 | 31.9319 | 11.0063 | 48.8906 | 22.1469 | 58.4526 | 59.4 | 12.7411 | 38.8804 | 47.0775 | 28.4041 | 36.5402 | 43.1974
177 | 53.8898 | 19.2275 | 8.6767 | 6.1427 | 18.6849 | 25.5591 | 8.2905 | 2.2201 | 6.6945 | 2.403 | 2.7432 | 1.1375 | 0.48302 | 1.4763 | 0.26535 | 3.9333 | 57.6434 | 57.7549 | 0.41015 | 9.2727 | 1.7291 | 3.6112 | 7.3001 | 12.1361
178 | 9.8699 | 6.0584 | 3.0344 | 0.33626 | 0.27058 | 0 | 0 | 0.33721 | 1.4281 | 4.167 | 8.9676 | 15.5509 | 31.3542 | 22.2525 | 55.134 | 20.506 | 14.326 | 1.6371 | 0.21815 | 0.29192 | 26.4862 | 56.7391 | 0.77957 | 0.92544
179 | 1.6514 | 3.3622 | 5.9561 | 3.9109 | 0.65433 | 1.6763 | 5.5031 | 12.393 | 16.2736 | 26.7852 | 40.7512 | 37.5284 | 31.9921 | 24.4624 | 41.8166 | 59.3642 | 59.1601 | 2.1219 | 52.8861 | 22.3362 | 1.8084 | 15.9547 | 22.2006 | 16.6821
180 | 35.5582 | 48.5017 | 27.2298 | 19.079 | 6.8773 | 1.8868 | 0 | 0.54323 | 0 | 0 | 2.6476 | 25.0979 | 20.8034 | 48.63 | 40.944 | 21.2358 | 41.2473 | 11.7494 | 43.132 | 55.6332 | 52.4336 | 59.0321 | 19.1684 | 19.7781
181 | 20.6411 | 22.3404 | 12.8457 | 11.982 | 7.7237 | 4.0577 | 4.6404 | 9.3024 | 14.9994 | 19.4626 | 36.0708 | 23.0086 | 32.861 | 33.3245 | 39.9216 | 22.3234 | 58.6303 | 14.572 | 0 | 7.2819 | 5.1471 | 1.569 | 0.40979 | 0
182 | 1.4627 | 0 | 1.405 | 4.1314 | 4.277 | 3.0357 | 4.6743 | 13.5764 | 16.0231 | 3.0228 | 8.2624 | 7.1893 | 11.5092 | 16.5075 | 50.8593 | 55.0582 | 40.1701 | 8.5764 | 3.1246 | 2.9989 | 4.8895 | 2.9803 | 0 | 0
183 | 0.13321 | 4.771 | 3.9471 | 9.9816 | 20.9806 | 51.754 | 25.8183 | 25.3085 | 26.1196 | 10.6214 | 4.3529 | 3.6954 | 11.6365 | 12.4259 | 7.0524 | 39.0016 | 37.0543 | 40.6456 | 34.3717 | 26.1835 | 45.0536 | 49.8464 | 27.4989 | 20.6878
184 | 17.3483 | 27.0888 | 15.8484 | 20.4233 | 46.1362 | 30.5733 | 37.7978 | 19.5705 | 12.8686 | 16.951 | 3.3539 | 2.3594 | 23.939 | 45.342 | 33.7473 | 59.4 | 59.4 | 49.2415 | 31.0156 | 42.4044 | 57.3554 | 38.6873 | 48.1962 | 55.7387
185 | 46.7326 | 45.0713 | 40.6401 | 37.1981 | 28.4627 | 20.806 | 8.7356 | 6.2232 | 21.1377 | 22.8897 | 20.4924 | 21.0796 | 24.1678 | 34.5529 | 17.9665 | 10.7024 | 17.4506 | 49.1163 | 18.8487 | 6.1692 | 9.7026 | 4.5688 | 7.2042 | 17.0893
186 | 41.9867 | 46.1178 | 39.0868 | 24.2115 | 17.3039 | 12.2703 | 7.8645 | 0 | 0 | 0.53789 | 3.313 | 2.7884 | 0.58728 | 0.042441 | 0.27391 | 1.169 | 3.603 | 9.4836 | 11.8046 | 16.6894 | 33.8564 | 25.5679 | 9.0988 | 1.4352
187 | 0 | 7.8631 | 16.0081 | 24.5316 | 25.8074 | 19.3416 | 8.8334 | 7.2696 | 5.8423 | 4.2404 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2964 | 6.5201 | 22.5554 | 16.0814 | 43.3179 | 59.3956 | 50.5302 | 28.4646
188 | 24.6717 | 32.3734 | 59.0853 | 49.8077 | 55.1297 | 59.2393 | 54.7906 | 47.6324 | 48.4204 | 57.9272 | 29.2676 | 0.40604 | 0 | 37.4428 | 59.4 | 59.2513 | 1.2795 | 31.6633 | 22.6575 | 13.2062 | 10.4048 | 19.3183 | 0 | 33.8616
189 | 8.244 | 0.48564 | 8.0148 | 0 | 3.884 | 3.0829 | 0 | 5.0862 | 4.7999 | 7.7132 | 8.7977 | 14.101 | 15.3507 | 11.1127 | 6.731 | 17.2153 | 34.3955 | 0.47607 | 8.6372 | 1.9485 | 15.9865 | 9.0289 | 4.9953 | 0.3217
190 | 3.3461 | 0 | 2.4519 | 0 | 0.6573 | 0 | 0 | 0 | 0.1253 | 7.5891 | 26.1206 | 20.9392 | 15.5673 | 12.607 | 7.0033 | 19.9301 | 5.0484 | 2.3919 | 7.7134 | 37.3086 | 14.5278 | 16.9422 | 7.1441 | 13.9023
191 | 12.2374 | 9.4651 | 4.3999 | 1.6682 | 0 | 0 | 0 | 1.8085 | 2.9128 | 0.12251 | 1.4135 | 1.9289 | 0.42596 | 0.029007 | 0.18052 | 0 | 1.4848 | 0.034119 | 3.3077 | 8.8394 | 55.6785 | 27.8341 | 0.88342 | 1.4334
192 | 4.2127 | 16.2351 | 17.1821 | 13.3038 | 10.4255 | 3.6125 | 2.8383 | 0.26451 | 2.8646 | 0.49087 | 0 | 0 | 2.1848 | 0.14533 | 22.5753 | 49.2523 | 52.0628 | 15.2592 | 4.2025 | 1.6392 | 4.8849 | 39.6314 | 24.3379 | 9.1798
193 | 22.1633 | 18.8438 | 2.4893 | 9.8223 | 3.6442 | 10.5946 | 20.9206 | 7.8558 | 1.0602 | 0 | 0 | 0 | 0 | 0 | 5.8217 | 8.6057 | 0.066455 | 0 | 8.5633 | 21.2341 | 30.2541 | 38.1915 | 44.6046 | 16.5056
194 | 30.2623 | 57.5066 | 35.5838 | 35.1131 | 47.5427 | 54.2176 | 39.3692 | 16.3414 | 9.4426 | 16.6545 | 19.6532 | 17.6345 | 7.8546 | 3.2041 | 0.21874 | 0 | 0 | 0 | 0.16097 | 0 | 0 | 0 | 10.2936 | 41.6659
195 | 48.5192 | 59.0622 | 57.8595 | 9.6586 | 26.873 | 14.0012 | 14.218 | 22.3252 | 0 | 0 | 0 | 0 | 1.5212 | 4.0823 | 7.1715 | 52.7848 | 8.8989 | 48.2054 | 57.4114 | 27.074 | 0 | 41.1863 | 35.1215 | 41.0966
196 | 0 | 0.12542 | 4.129 | 5.299 | 0.30785 | 0.058669 | 0 | 0 | 0 | 2.4512 | 5.21 | 9.9478 | 10.9904 | 8.9905 | 9.2349 | 14.8622 | 24.7221 | 13.7496 | 6.9683 | 33.033 | 19.2926 | 5.5776 | 8.9547 | 27.2476
197 | 26.6777 | 26.1652 | 15.7573 | 18.2844 | 23.4629 | 17.451 | 5.3336 | 0.068952 | 0 | 0.97401 | 4.3118 | 6.5795 | 4.52 | 2.4538 | 2.2068 | 0.99327 | 0.41781 | 0 | 16.4081 | 59.4 | 59.341 | 42.2213 | 57.7152 | 40.6997
198 | 59.2788 | 59.4 | 54.8435 | 27.6438 | 32.9399 | 28.3656 | 12.4742 | 1.7383 | 5.0293 | 17.4173 | 17.134 | 10.0581 | 7.2012 | 8.0695 | 7.7189 | 9.2648 | 5.6544 | 36.6902 | 5.8928 | 57.9941 | 22.9679 | 34.3492 | 6.3481 | 1.9718
199 | 6.1879 | 16.5993 | 5.2537 | 6.5431 | 4.4462 | 2.4877 | 0.060987 | 3.2714 | 1.4843 | 2.8528 | 5.183 | 1.4915 | 5.0938 | 6.3051 | 4.5375 | 15.94 | 33.6105 | 26.1477 | 24.7111 | 19.6684 | 46.6 | 3.7855 | 59.4 | 59.4
200 | 53.9022 | 59.3309 | 20.9851 | 11.8936 | 47.89 | 25.5682 | 18.936 | 7.34 | 1.0104 | 0 | 0 | 0 | 0 | 0 | 0.35748 | 0.98792 | 4.1867 | 13.6417 | 59.1648 | 59.062 | 41.7091 | 59.2933 | 58.1195 | 34.3704
201 | 57.8438 | 58.4742 | 45.456 | 0 | 0 | 3.4557 | 1.1544 | 0 | 0.13689 | 7.6053 | 59.2564 | 42.5701 | 1.6046 | 5.5481 | 58.2974 | 39.5504 | 5.6857 | 50.0314 | 59.4 | 54.6048 | 6.5956 | 32.4489 | 58.8321 | 58.7991
202 | 39.9704 | 53.5307 | 38.6758 | 17.3262 | 5.8789 | 9.7514 | 54.0279 | 23.1444 | 16.9734 | 2.4452 | 0 | 2.645 | 3.5437 | 4.5766 | 5.3425 | 4.3392 | 14.6355 | 30.1093 | 53.7293 | 59.4 | 53.5115 | 29.4452 | 14.8546 | 51.4141
203 | 59.2224 | 21.094 | 51.2748 | 53.0592 | 40.596 | 40.8967 | 35.0595 | 27.8697 | 16.0883 | 8.9235 | 0.93977 | 0.77755 | 5.2869 | 6.0233 | 8.0836 | 19.6982 | 13.8221 | 20.3537 | 16.6825 | 26.9726 | 32.4782 | 32.0997 | 43.2377 | 31.2599
204 | 16.5447 | 24.6361 | 14.6641 | 9.4281 | 5.236 | 8.6767 | 16.1012 | 4.5142 | 0.18403 | 0 | 0 | 3.1162 | 4.85 | 5.1426 | 11.6491 | 28.2556 | 59.4 | 17.7915 | 5.1776 | 0.27105 | 13.7752 | 51.8589 | 59.2332 | 59.3907
205 | 29.3557 | 59.0836 | 59.4 | 47.5779 | 9.3265 | 6.0832 | 6.2721 | 0 | 0 | 0 | 0 | 0.061878 | 2.5333 | 6.4751 | 10.8974 | 13.4544 | 22.9605 | 37.4636 | 25.8537 | 59.3303 | 59.275 | 58.4607 | 59.3958 | 40.6781
206 | 44.8043 | 55.6482 | 30.7286 | 24.4733 | 18.1032 | 9.7183 | 6.7437 | 12.415 | 59.4 | 59.4 | 46.9882 | 48.5828 | 35.0436 | 9.9848 | 0.17078 | 3.2542 | 13.3394 | 5.1073 | 3.3989 | 6.5743 | 8.8358 | 2.2124 | 0.078403 | 7.3259
207 | 13.3744 | 3.3568 | 2.0662 | 0.30523 | 1.2363 | 1.5937 | 0.19919 | 1.1847 | 0.804 | 3.3282 | 7.989 | 16.6032 | 19.3619 | 14.1412 | 19.4622 | 10.9447 | 0 | 2.293 | 1.7242 | 0 | 0.21773 | 21.6288 | 17.1203 | 51.8896
208 | 58.2929 | 12.5606 | 24.6335 | 7.9422 | 5.4757 | 1.1421 | 3.4821 | 0 | 2.4147 | 15.9494 | 36.6736 | 52.4536 | 51.6089 | 52.136 | 50.348 | 59.1478 | 59.4 | 59.363 | 13.1968 | 57.1389 | 38.5882 | 59.0657 | 36.9145 | 3.4974
209 | 7.0172 | 3.2517 | 0 | 6.0248 | 33.8134 | 35.0283 | 17.7212 | 17.2756 | 8.0125 | 0 | 0 | 0.34066 | 0 | 0 | 57.5278 | 0 | 0.039112 | 29.3279 | 32.7095 | 4.8958 | 24.1595 | 20.9419 | 22.5224 | 27.7313
210 | 14.6157 | 18.2876 | 56.6664 | 58.3763 | 51.7993 | 57.8429 | 38.8569 | 17.1824 | 23.0133 | 24.3645 | 1.4239 | 0 | 0 | 3.246 | 17.2898 | 52.5011 | 0.8194 | 14.6301 | 9.5282 | 33.5971 | 27.663 | 8.4751 | 21.5082 | 26.806
211 | 39.4641 | 14.3363 | 18.1334 | 10.7909 | 4.0421 | 2.0215 | 0.058015 | 0 | 0 | 0 | 0 | 6.0927 | 8.3178 | 21.5376 | 19.1307 | 57.1487 | 36.6212 | 33.6014 | 0 | 12.9733 | 43.3029 | 13.8101 | 44.5736 | 48.584
212 | 45.9773 | 1.2741 | 0.79313 | 0.42382 | 0.89655 | 4.4995 | 2.5052 | 4.6752 | 5.5448 | 8.4799 | 2.4969 | 0 | 1.1722 | 7.7118 | 4.9552 | 43.1974 | 30.7746 | 47.5695 | 9.9793 | 58.932 | 41.9208 | 28.9635 | 9.2984 | 34.3568
213 | 35.1239 | 38.9714 | 33.6028 | 26.4544 | 22.0007 | 8.0521 | 2.0064 | 0 | 0 | 0 | 0 | 4.4062 | 1.7114 | 0 | 1.0982 | 1.9014 | 20.021 | 53.2825 | 15.2511 | 1.4186 | 0.66337 | 0.23557 | 10.8071 | 14.4556
214 | 5.4017 | 21.9732 | 17.9959 | 19.3207 | 26.5037 | 16.3363 | 19.4808 | 6.0713 | 6.6952 | 8.0985 | 5.6116 | 1.0744 | 1.9295 | 1.255 | 1.1477 | 0.917 | 7.2067 | 7.1044 | 11.1749 | 18.8285 | 22.2669 | 58.6312 | 50.2484 | 43.7373
215 | 58.7344 | 50.0465 | 56.5822 | 59.4 | 58.135 | 57.4078 | 57.4752 | 45.9644 | 23.139 | 0.44629 | 0 | 0 | 0 | 12.788 | 58.9345 | 10.5418 | 34.358 | 26.4704 | 53.7592 | 0.94785 | 13.1346 | 14.4678 | 12.7954 | 11.4125
216 | 14.9625 | 11.426 | 12.6816 | 11.456 | 13.1851 | 18.6409 | 11.7711 | 3.9407 | 0 | 0 | 0 | 0 | 0 | 2.9085 | 57.1549 | 57.9105 | 26.972 | 57.3337 | 35.6453 | 59.4 | 59.4 | 45.0818 | 59.4 | 56.9494
217 | 53.0039 | 42.854 | 37.8206 | 19.396 | 1.8636 | 1.3591 | 0.060036 | 0 | 0 | 0 | 0 | 0.69796 | 8.5609 | 33.1756 | 11.2571 | 7.5605 | 2.4953 | 11.7945 | 10.36 | 24.4142 | 13.7118 | 16.192 | 38.2597 | 54.4228
218 | 55.3333 | 48.8722 | 52.2162 | 34.416 | 17.8294 | 16.2696 | 13.3931 | 11.0302 | 19.8076 | 25.5868 | 58.2911 | 44.9282 | 29.1825 | 21.1248 | 23.2953 | 59.2989 | 59.4 | 53.6777 | 58.507 | 59.4 | 59.4 | 57.7382 | 57.7606 | 58.9078
219 | 59.3289 | 57.1825 | 53.7019 | 36.2376 | 25.1592 | 19.6019 | 8.0291 | 0.41514 | 0 | 0 | 0 | 1.8015 | 3.6018 | 4.8573 | 4.1413 | 4.6835 | 5.0303 | 6.9173 | 7.9355 | 7.1825 | 12.7299 | 8.5599 | 6.1119 | 13.2058
220 | 43.2701 | 29.7168 | 20.8044 | 6.4121 | 0 | 0 | 0 | 0 | 0 | 3.913 | 6.4704 | 15.238 | 30.2449 | 45.9333 | 55.5904 | 59.4 | 59.4 | 8.339 | 12.6418 | 37.8604 | 0.34054 | 29.329 | 52.87 | 20.1921
221 | 0 | 3.0461 | 0.42994 | 1.236 | 6.8978 | 12.6792 | 12.0367 | 2.1684 | 3.6892 | 5.0913 | 0 | 4.6673 | 2.8727 | 0.11318 | 8.3656 | 55.7154 | 38.974 | 55.0408 | 48.1917 | 54.9772 | 22.9262 | 0 | 2.8533 | 6.1701
222 | 15.8767 | 14.3259 | 55.105 | 59.4 | 59.2486 | 59.079 | 49.4985 | 40.3789 | 20.6977 | 10.4593 | 0 | 0.093264 | 0 | 3.1952 | 7.4903 | 3.948 | 0 | 59.4 | 59.4 | 59.4 | 59.4 | 59.209 | 58.5562 | 43.2014
223 | 55.3418 | 56.9578 | 42.6567 | 36.0122 | 17.2468 | 11.3013 | 7.6391 | 2.3196 | 0 | 0 | 0 | 0 | 2.604 | 11.5876 | 10.8601 | 5.7688 | 35.0579 | 57.865 | 59.4 | 52.6455 | 1.7771 | 24.9382 | 48.2552 | 27.8256
224 | 57.6315 | 58.5637 | 26.6692 | 32.5886 | 20.2837 | 15.5693 | 13.7163 | 5.4149 | 3.6531 | 3.4028 | 5.4852 | 0.9812 | 2.2423 | 16.9716 | 17.8715 | 0.032277 | 5.8061 | 37.5281 | 49.5387 | 30.6196 | 54.2969 | 40.2387 | 40.391 | 39.0865
225 | 35.0336 | 27.0893 | 34.9121 | 28.1188 | 26.4938 | 42.2736 | 49.8358 | 30.0403 | 12.0538 | 3.259 | 0 | 0 | 4.6807 | 3.7783 | 0.11371 | 2.3215 | 13.3591 | 10.4881 | 10.3823 | 20.779 | 54.7749 | 58.0342 | 59.1863 | 59.3916
226 | 59.4 | 59.3622 | 59.3252 | 58.6634 | 59.2655 | 59.4 | 58.7872 | 39.8919 | 25.8354 | 16.8256 | 9.8118 | 0 | 0 | 0 | 0 | 0 | 3.5772 | 6.9189 | 35.1109 | 59.4 | 59.4 | 59.4 | 59.1532 | 52.5427
227 | 23.8085 | 21.0153 | 15.9324 | 8.0819 | 6.9564 | 2.927 | 1.5883 | 4.3882 | 3.0476 | 4.0275 | 0 | 0 | 0 | 2.6688 | 26.0426 | 35.7287 | 59.0195 | 59.2008 | 40.4026 | 37.5129 | 0.73113 | 0 | 0.74682 | 5.5258
228 | 14.1677 | 0.062116 | 0 | 8.5127 | 0.70135 | 0 | 1.5371 | 4.1281 | 10.6958 | 20.1187 | 20.8985 | 26.9597 | 13.5604 | 8.469 | 3.2895 | 52.503 | 51.1978 | 29.0171 | 12.6416 | 31.1351 | 11.3141 | 56.0549 | 2.6026 | 4.1276
229 | 3.575 | 14.7013 | 21.1329 | 16.3921 | 14.3373 | 8.8536 | 5.2269 | 1.4777 | 0 | 0 | 0 | 5.3071 | 4.4011 | 15.2857 | 59.3474 | 26.1984 | 22.6295 | 8.0683 | 13.668 | 46.5481 | 50.7673 | 45.0639 | 46.4485 | 27.6042
230 | 5.1668 | 12.6824 | 12.8949 | 19.0983 | 14.8457 | 14.7507 | 11.9323 | 1.8308 | 0.57842 | 0 | 0 | 0 | 2.5783 | 1.9254 | 2.2215 | 1.6613 | 0 | 0 | 1.024 | 49.722 | 59.2715 | 45.3274 | 58.0473 | 28.0731
231 | 32.9248 | 18.8557 | 16.2142 | 18.2507 | 19.5281 | 12.6847 | 13.7814 | 6.9128 | 10.264 | 17.6634 | 14.8719 | 15.8511 | 10.6347 | 8.1739 | 9.2676 | 58.5733 | 0 | 0 | 0 | 0 | 4.7359 | 0 | 1.8662 | 14.5606
232 | 30.7325 | 24.3763 | 53.6354 | 51.3219 | 5.9431 | 15.8407 | 10.2638 | 0 | 1.4033 | 1.1749 | 4.3362 | 0 | 1.8611 | 4.1746 | 7.3005 | 10.5173 | 0.85851 | 55.4541 | 44.5215 | 33.8331 | 3.93 | 48.8864 | 3.59 | 0.72673
233 | 4.2848 | 7.0418 | 2.8452 | 0.20448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.318 | 1.8442 | 2.4317 | 3.4783 | 3.3352 | 22.714 | 1.2099 | 2.2752 | 6.9488 | 2.7508 | 1.3965 | 38.6521 | 34.6254
234 | 36.4842 | 17.296 | 13.7773 | 11.3825 | 7.6281 | 5.1336 | 6.8909 | 4.8435 | 11.9748 | 11.9549 | 5.8786 | 9.2367 | 10.7551 | 8.0953 | 14.5603 | 2.1038 | 29.0554 | 33.8027 | 22.5972 | 18.2162 | 9.2935 | 18.4941 | 7.1696 | 6.4404
235 | 10.7476 | 4.761 | 1.2086 | 2.0696 | 2.4018 | 0.51821 | 0 | 1.1976 | 1.3068 | 4.2057 | 6.4324 | 9.6432 | 12.2502 | 21.999 | 33.1945 | 41.5127 | 58.3561 | 58.8765 | 57.1805 | 37.4925 | 35.2566 | 37.5623 | 48.3237 | 35.029
236 | 18.5293 | 11.1295 | 2.9251 | 0.57474 | 0.55578 | 2.2501 | 0.98102 | 2.1152 | 2.4676 | 10.2478 | 20.5336 | 24.5445 | 50.3277 | 37.4992 | 45.9214 | 40.9767 | 51.7902 | 56.909 | 58.4638 | 59.4 | 39.4026 | 13.4713 | 5.5752 | 1.4412
237 | 5.9456 | 10.4177 | 7.8406 | 4.264 | 1.4447 | 1.0186 | 1.3004 | 1.5177 | 0.93953 | 7.3411 | 7.0059 | 5.057 | 2.6207 | 4.4661 | 5.6821 | 5.6547 | 54.4999 | 55.8961 | 0.99986 | 1.8367 | 0.65023 | 0 | 10.394 | 4.7631
238 | 10.981 | 7.5285 | 9.868 | 15.5757 | 20.5003 | 9.8285 | 4.3588 | 0 | 0 | 0 | 2.3055 | 4.9311 | 6.4816 | 6.0593 | 8.0878 | 3.8309 | 11.4814 | 8.7171 | 10.3414 | 14.6909 | 14.8725 | 12.9938 | 6.9897 | 18.1287
239 | 8.4809 | 2.985 | 5.174 | 0.73618 | 0 | 0.62384 | 0 | 3.3745 | 1.0203 | 2.2025 | 2.3155 | 4.1053 | 0 | 0.82891 | 15.8193 | 20.2718 | 49.9839 | 50.6611 | 30.3791 | 20.7546 | 25.2162 | 17.2416 | 30.8696 | 29.0255
240 | 15.5546 | 7.2167 | 13.7232 | 16.1604 | 16.3133 | 13.0684 | 5.4337 | 0 | 0 | 0 | 0 | 8.167 | 7.4707 | 7.7795 | 48.633 | 14.5224 | 10.8199 | 3.0117 | 9.0696 | 58.0681 | 11.2342 | 15.3166 | 5.5135 | 4.1409
241 | 7.7408 | 25.9961 | 40.8121 | 16.9715 | 11.7695 | 15.2821 | 11.0945 | 8.4062 | 16.3737 | 19.902 | 12.504 | 7.2401 | 5.7403 | 4.6652 | 4.8602 | 4.7746 | 4.446 | 1.0767 | 0 | 0 | 0.84092 | 0 | 18.2559 | 26.1
242 | 12.9743 | 17.9272 | 26.4742 | 32.0524 | 58.0551 | 51.1584 | 55.344 | 39.7942 | 25.7364 | 3.6927 | 0 | 0 | 0 | 0 | 0 | 3.0694 | 7.6638 | 20.0909 | 23.0791 | 31.7179 | 50.2254 | 58.5217 | 59.4 | 59.3836
243 | 55.1093 | 11.8375 | 2.9863 | 4.3617 | 11.1678 | 13.8775 | 9.2551 | 2.8925 | 3.1202 | 2.5682 | 3.06 | 1.8446 | 0.19265 | 3.3057 | 4.1524 | 3.4604 | 5.4518 | 3.2045 | 1.2237 | 0 | 0 | 5.7643 | 22.4549 | 26.2618
244 | 20.98 | 12.7917 | 7.3123 | 11.7198 | 20.3098 | 20.6056 | 15.5684 | 10.4647 | 9.7265 | 3.1566 | 4.524 | 3.6528 | 3.8402 | 4.5524 | 4.2067 | 6.3292 | 9.571 | 10.2023 | 6.5429 | 10.5457 | 15.8005 | 16.0539 | 9.8686 | 42.8964
245 | 31.7387 | 15.2489 | 20.1505 | 19.5729 | 18.3652 | 20.8038 | 26.8853 | 23.0505 | 32.5901 | 23.8877 | 14.3659 | 4.6689 | 0.88544 | 3.4875 | 5.0715 | 5.6875 | 34.4477 | 18.9103 | 23.4639 | 59.4 | 58.8597 | 35.6535 | 25.4347 | 24.9141
246 | 29.9794 | 18.0412 | 27.4479 | 23.1599 | 18.5479 | 13.6694 | 52.5261 | 19.4032 | 2.0829 | 7.5237 | 9.6155 | 3.7253 | 0.28579 | 0 | 0 | 0.088627 | 1.542 | 10.0894 | 8.7196 | 3.9392 | 18.1268 | 58.3977 | 22.0217 | 59.0921
247 | 39.4107 | 52.1455 | 55.5029 | 6.4601 | 12.0513 | 7.9134 | 3.3179 | 0.70575 | 0 | 0 | 0 | 3.2028 | 0 | 0 | 0 | 8.286 | 42.1899 | 36.2706 | 59.3656 | 59.4 | 59.4 | 25.257 | 53.9428 | 17.8818
248 | 9.7232 | 18.3459 | 37.0417 | 51.6715 | 56.6484 | 55.0389 | 56.4186 | 52.3437 | 28.5098 | 17.7603 | 0.62015 | 7.0137 | 17.9999 | 19.9142 | 16.0524 | 20.7861 | 14.0086 | 10.3866 | 14.8873 | 59.4 | 59.4 | 59.4 | 58.9538 | 51.6549
249 | 33.5308 | 18.4255 | 35.2437 | 50.5292 | 55.8878 | 55.9134 | 58.0162 | 51.7494 | 24.7915 | 10.0839 | 0.31605 | 0 | 7.8212 | 6.9056 | 6.069 | 7.6886 | 36.7881 | 55.254 | 59.3889 | 59.2525 | 58.9974 | 59.2806 | 58.3631 | 23.4506
250 | 14.2233 | 26.6379 | 39.0834 | 28.4355 | 32.2906 | 14.6695 | 7.4148 | 2.2321 | 0 | 0 | 0 | 0 | 2.6676 | 13.2618 | 16.0576 | 31.948 | 45.3266 | 59.4 | 59.4 | 59.4 | 59.4 | 57.3392 | 47.6185 | 36.3641
251 | 4.2614 | 4.7956 | 4.823 | 4.1657 | 4.3355 | 4.9697 | 4.0124 | 0 | 0 | 0 | 5.3396 | 10.9152 | 12.7789 | 14.958 | 14.3876 | 14.1806 | 14.552 | 19.6155 | 25.6499 | 27.2191 | 43.4303 | 28.9241 | 8.4677 | 10.3761
252 | 3.5823 | 6.6396 | 6.4031 | 4.9324 | 3.3152 | 2.8559 | 1.4573 | 0 | 0 | 0 | 5.5407 | 11.1182 | 14.0194 | 8.0054 | 5.9314 | 39.7927 | 0.30749 | 10.524 | 9.85 | 4.8988 | 3.1343 | 13.0293 | 1.4725 | 34.7925
253 | 58.2292 | 44.7244 | 40.3617 | 58.1238 | 48.5906 | 48.8723 | 26.3749 | 14.8083 | 9.469 | 22.798 | 34.6235 | 23.9225 | 9.8087 | 5.218 | 1.9598 | 0.92871 | 0.87016 | 13.5642 | 36.4234 | 58.0937 | 58.5316 | 8.8062 | 22.2404 | 5.7353
254 | 32.2676 | 31.3818 | 17.5234 | 22.5545 | 23.5522 | 23.6389 | 22.2163 | 18.3377 | 23.6968 | 25.6194 | 43.0188 | 30.0081 | 27.5583 | 22.6547 | 16.0695 | 25.421 | 24.4912 | 14.9192 | 3.297 | 0 | 0.93032 | 16.3077 | 47.9649 | 9.1004
255 | 15.8771 | 11.4492 | 12.4622 | 9.5909 | 10.3292 | 7.8799 | 11.5163 | 4.3207 | 10.7436 | 15.7781 | 9.0932 | 7.831 | 3.3059 | 3.6574 | 7.3995 | 11.8734 | 14.8174 | 36.6333 | 6.1469 | 7.365 | 2.7463 | 1.1117 | 0.2172 | 21.3552
256 | 28.6631 | 33.7734 | 34.507 | 11.039 | 9.8759 | 15.954 | 19.6243 | 11.8509 | 14.3368 | 38.9142 | 35.1643 | 0 | 8.634 | 6.4695 | 6.6147 | 57.7297 | 21.349 | 36.5251 | 35.7366 | 8.963 | 26.2073 | 43.8321 | 26.3976 | 10.3631
257 | 6.0568 | 14.0471 | 0.33127 | 0 | 0 | 0.91552 | 1.5917 | 0.5572 | 0 | 6.88 | 7.7872 | 12.0232 | 9.8482 | 6.3621 | 10.1395 | 7.4918 | 4.5332 | 1.3286 | 6.9706 | 6.9964 | 5.8997 | 0 | 0 | 18.1535
258 | 41.8776 | 21.3172 | 28.6704 | 37.9452 | 54.3668 | 58.7977 | 58.2831 | 58.5354 | 59.3995 | 59.1923 | 36.8889 | 4.0181 | 0.91902 | 0 | 0 | 0 | 27.8227 | 58.4088 | 59.4 | 59.2813 | 59.4 | 58.4932 | 57.8501 | 58.2661
259 | 59.4 | 58.3984 | 52.6988 | 43.3226 | 38.4293 | 30.4823 | 27.1663 | 16.4883 | 8.8029 | 2.913 | 0.067704 | 0 | 0 | 0 | 3.0312 | 9.3724 | 5.0672 | 18.8621 | 21.8786 | 12.9509 | 17.7762 | 39.9981 | 10.0402 | 4.2534
260 | 10.6013 | 9.2966 | 25.2115 | 33.5974 | 31.8041 | 33.1779 | 27.7903 | 36.9569 | 19.6 | 8.6491 | 12.0353 | 4.1665 | 1.3733 | 3.6166 | 2.7241 | 2.469 | 30.5335 | 6.0835 | 27.4129 | 55.4908 | 46.839 | 53.3589 | 51.8406 | 56.4544
261 | 59.4 | 58.8577 | 56.2557 | 42.0249 | 13.1379 | 10.7043 | 10.8335 | 7.2272 | 2.8122 | 0 | 0 | 3.4943 | 11.3168 | 25.9481 | 29.8236 | 31.2445 | 31.2705 | 42.3049 | 19.475 | 0.7423 | 0 | 0 | 0.60398 | 2.8401
262 | 12.6569 | 23.0409 | 0 | 0.15342 | 0 | 9.4579 | 7.0994 | 0 | 0 | 0 | 7.2593 | 25.0576 | 52.0219 | 58.6379 | 58.3343 | 49.0786 | 31.8819 | 17.4588 | 12.2927 | 24.2429 | 17.839 | 17.7189 | 19.3197 | 14.5719
263 | 16.1185 | 24.219 | 26.1287 | 27.6816 | 26.8618 | 31.0222 | 28.1108 | 15.2198 | 36.7698 | 59.4 | 59.3657 | 59.4 | 59.4 | 0.55697 | 0.43428 | 0 | 11.4141 | 8.1753 | 37.0952 | 34.9549 | 37.5163 | 27.4493 | 29.1573 | 35.5335
264 | 44.449 | 43.4045 | 32.9759 | 30.5073 | 29.8245 | 17.8305 | 19.913 | 25.8542 | 57.5101 | 50.1529 | 48.0833 | 45.6402 | 49.6837 | 47.5497 | 33.3351 | 32.9599 | 33.1273 | 17.6165 | 9.8794 | 9.6277 | 9.7944 | 9.012 | 2.0238 | 1.7727
265 | 0.097306 | 0 | 1.8537 | 7.8083 | 12.3363 | 6.7527 | 5.2632 | 8.518 | 9.2616 | 9.3328 | 10.5163 | 15.0946 | 20.4214 | 19.2995 | 20.3568 | 32.373 | 40.2753 | 59.391 | 59.4 | 59.4 | 59.2866 | 59.4 | 49.1473 | 19.4642
266 | 13.004 | 6.0343 | 3.131 | 6.2916 | 10.3907 | 11.2077 | 8.7218 | 5.7622 | 0.6167 | 0 | 0.029007 | 0 | 0 | 2.0846 | 1.2742 | 1.2501 | 2.6479 | 6.4142 | 28.1689 | 59.049 | 59.3236 | 56.9035 | 59.4 | 59.3746
267 | 59.3897 | 55.1634 | 26.7731 | 5.3783 | 12.489 | 17.8102 | 23.8034 | 34.4632 | 27.7242 | 10.1153 | 5.5553 | 1.7996 | 0 | 2.9488 | 10.5114 | 5.2316 | 19.5276 | 55.789 | 59.4 | 59.3481 | 59.1384 | 58.9996 | 58.5772 | 58.9924
268 | 59.0972 | 59.395 | 59.3633 | 59.4 | 59.4 | 59.4 | 56.8977 | 26.0039 | 34.5392 | 25.281 | 8.5382 | 5.0362 | 0.97781 | 23.1393 | 16.9467 | 58.0748 | 36.9377 | 58.1154 | 21.8693 | 16.1452 | 31.0128 | 14.5025 | 17.7792 | 4.3072
269 | 0 | 2.7426 | 2.3416 | 1.06 | 1.6291 | 2.8587 | 5.1042 | 4.4332 | 0.90933 | 1.9103 | 2.089 | 0 | 0 | 8.8316 | 14.8441 | 22.8812 | 18.8622 | 26.4411 | 43.4099 | 45.601 | 36.8029 | 59.4 | 40.0255 | 8.5168
270 | 23.2954 | 30.7176 | 27.2797 | 24.648 | 30.4662 | 39.1217 | 31.1564 | 27.2457 | 16.3454 | 9.47 | 5.2481 | 0.56975 | 0 | 0 | 4.1743 | 5.9599 | 9.4293 | 20.7757 | 49.7665 | 21.2561 | 2.0806 | 20.2649 | 25.0453 | 20.1203
271 | 12.1461 | 10.6678 | 11.1349 | 12.9114 | 8.4158 | 1.9318 | 0 | 0 | 0 | 0 | 3.2742 | 4.6505 | 7.041 | 10.4693 | 15.253 | 18.6866 | 26.2162 | 14.7051 | 24.9093 | 8.8678 | 6.3089 | 6.8472 | 9.8201 | 16.8429
272 | 9.9913 | 17.9625 | 14.9376 | 56.4414 | 40.4502 | 59.4 | 58.913 | 57.4738 | 11.6892 | 12.7509 | 1.8687 | 4.9879 | 4.4875 | 5.3067 | 4.7327 | 10.1308 | 7.2014 | 14.5516 | 16.4622 | 11.6618 | 5.8138 | 4.0038 | 7.305 | 10.9357
273 | 6.5943 | 10.7851 | 11.704 | 8.7673 | 6.3797 | 1.7413 | 0 | 0 | 0 | 0 | 2.4709 | 1.9502 | 1.0598 | 2.2402 | 2.7394 | 3.0327 | 2.9384 | 10.1336 | 17.3946 | 13.3223 | 20.1418 | 14.765 | 22.5727 | 21.6544
274 | 24.5354 | 19.9889 | 11.8037 | 15.8061 | 6.0321 | 2.1927 | 7.8101 | 8.631 | 2.4864 | 1.475 | 1.6449 | 2.7315 | 1.0949 | 4.0009 | 47.2213 | 6.3679 | 0 | 0 | 11.6924 | 57.7788 | 32.7946 | 29.752 | 56.0405 | 55.7854
275 | 31.1307 | 58.0972 | 59.3966 | 58.5976 | 42.4891 | 45.6889 | 22.1122 | 17.6964 | 10.3749 | 15.3025 | 17.8629 | 6.7943 | 1.9245 | 1.1511 | 4.7106 | 20.3391 | 31.1539 | 15.748 | 5.8751 | 56.5757 | 18.8671 | 0 | 1.8105 | 14.0064
276 | 10.4049 | 0 | 1.2351 | 8.2843 | 15.5112 | 13.828 | 0.72851 | 0 | 0 | 0.46721 | 0 | 2.6562 | 10.4323 | 10.1677 | 27.1308 | 0 | 59.3006 | 56.6432 | 59.3541 | 57.2811 | 55.7248 | 42.6997 | 36.5166 | 57.7708
277 | 56.5219 | 59.363 | 57.9859 | 54.549 | 55.9694 | 41.8848 | 5.6532 | 0 | 0 | 0 | 1.2405 | 5.7645 | 16.8456 | 32.8509 | 45.6147 | 57.9855 | 58.8193 | 28.6119 | 12.9711 | 10.095 | 2.4131 | 2.4265 | 0.39083 | 2.0276
278 | 2.5581 | 5.102 | 11.6329 | 11.6635 | 7.7343 | 40.8992 | 23.8343 | 4.3477 | 2.7537 | 0.035189 | 0.88782 | 3.8271 | 2.6282 | 10.8372 | 24.2842 | 34.1903 | 44.8982 | 48.7 | 42.9531 | 28.3953 | 10.7364 | 5.1855 | 0 | 0
279 | 0 | 1.0358 | 7.1251 | 8.1805 | 4.2115 | 2.5578 | 1.7778 | 0.18367 | 0 | 0 | 0.63151 | 2.4046 | 3.8897 | 11.6935 | 21.3264 | 39.0907 | 32.2783 | 49.2893 | 36.8956 | 17.5663 | 21.7172 | 32.6646 | 30.4881 | 27.0282
280 | 15.9997 | 15.4898 | 23.9797 | 43.8566 | 57.9979 | 59.3773 | 59.4 | 59.3783 | 53.3343 | 42.5114 | 59.3404 | 52.1118 | 31.3376 | 25.2213 | 18.1931 | 15.4836 | 13.3069 | 19.9683 | 26.4291 | 31.8899 | 59.4 | 57.1351 | 54.7622 | 56.1923
281 | 31.4752 | 24.5698 | 6.9851 | 25.6031 | 14.1066 | 30.9423 | 32.4686 | 29.2786 | 21.2485 | 16.5613 | 13.2707 | 20.8259 | 14.4384 | 27.0209 | 23.9878 | 18.5557 | 30.1667 | 19.6089 | 8.3673 | 6.9621 | 3.4858 | 1.2969 | 3.3381 | 0
282 | 0.8446 | 3.1068 | 3.2595 | 3.766 | 0.66616 | 0 | 0.033763 | 0 | 0.75841 | 2.5601 | 6.1662 | 6.3382 | 7.6566 | 8.547 | 18.0141 | 31.4494 | 32.1268 | 19.1856 | 10.3047 | 11.4607 | 9.437 | 6.565 | 6.7566 | 3.534
283 | 5.1187 | 2.1948 | 2.7144 | 3.8909 | 4.9405 | 2.7698 | 1.1274 | 0.94417 | 1.3558 | 2.8865 | 0 | 0 | 0.41234 | 6.3888 | 1.7146 | 0.04785 | 4.0412 | 1.5178 | 2.3976 | 22.7543 | 51.1654 | 52.8696 | 53.5129 | 57.0944
284 | 59.2207 | 59.4 | 59.4 | 59.4 | 59.4 | 59.3945 | 58.0032 | 41.5857 | 33.3962 | 59.133 | 58.2555 | 39.9745 | 22.1411 | 9.4767 | 13.7463 | 33.1004 | 43.4032 | 49.763 | 59.1734 | 58.1201 | 49.99 | 45.7432 | 46.0306 | 45.1649
285 | 43.6596 | 40.5359 | 36.0555 | 18.5205 | 7.6603 | 3.2875 | 0.6129 | 2.5609 | 2.6009 | 0.41009 | 1.0675 | 2.0748 | 4.9333 | 10.5617 | 13.1695 | 21.1453 | 31.9818 | 36.472 | 20.4957 | 9.7785 | 1.0991 | 0.65243 | 2.3453 | 5.8258
286 | 10.7309 | 13.0164 | 21.3631 | 23.2202 | 17.9704 | 21.0146 | 19.3784 | 13.3455 | 0.28431 | 0 | 0 | 0 | 0 | 0.91789 | 15.1386 | 38.0509 | 52.5566 | 56.2012 | 53.7199 | 40.686 | 7.2823 | 2.2798 | 0 | 0.67751
287 | 4.1113 | 8.7855 | 12.8472 | 16.8994 | 21.6824 | 21.7979 | 19.3504 | 15.6557 | 1.8151 | 0 | 0 | 0.98869 | 11.7189 | 26.3792 | 22.2391 | 12.1214 | 40.8452 | 0.030375 | 4.0495 | 6.3888 | 12.8021 | 7.2439 | 1.2415 | 0
288 | 0 | 1.6057 | 10.5742 | 34.0537 | 58.256 | 58.6507 | 55.7689 | 58.1987 | 59.1694 | 52.8102 | 23.6513 | 4.1325 | 2.8247 | 0.29418 | 2.2722 | 5.8604 | 0.038399 | 0.70717 | 2.3597 | 37.7586 | 40.0196 | 56.4716 | 57.154 | 47.1059
289 | 29.9274 | 17.0291 | 26.8732 | 43.7555 | 28.9808 | 8.5492 | 1.0073 | 0 | 5.9447 | 10.0867 | 7.9487 | 8.8091 | 6.5868 | 5.6548 | 6.2642 | 13.772 | 22.1441 | 18.5775 | 9.3036 | 8.1197 | 0 | 0 | 3.2755 | 40.2197
290 | 23.3617 | 32.276 | 53.2562 | 58.6185 | 56.584 | 57.0608 | 59.4 | 57.453 | 41.0105 | 32.8329 | 16.108 | 0.033822 | 0 | 0 | 0 | 2.4744 | 0.31997 | 18.3006 | 34.2652 | 14.4464 | 39.2585 | 45.618 | 52.4122 | 39.171
291 | 40.9727 | 30.726 | 30.6726 | 27.5618 | 27.1235 | 25.1484 | 24.7535 | 15.4419 | 2.5614 | 1.3604 | 0.71395 | 0.37935 | 2.5092 | 5.7383 | 11.0726 | 18.0079 | 48.4866 | 56.0318 | 43.2551 | 21.8918 | 13.0695 | 10.6051 | 3.57 | 0.27254
292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.45485 | 2.0043 | 4.4359 | 18.4198 | 20.1878 | 16.8323 | 13.0787 | 10.8593 | 15.4902 | 12.3612 | 8.7979 | 4.9312 | 0 | 0 | 0 | 4.4111 | 4.5283
293 | 4.9166 | 4.4074 | 1.14 | 0.77309 | 0.6189 | 1.3772 | 1.6254 | 2.2907 | 2.151 | 0.96996 | 0 | 1.2063 | 7.6113 | 10.3139 | 14.1571 | 24.3232 | 24.2867 | 30.0632 | 32.3963 | 16.4539 | 6.466 | 3.5599 | 0 | 0
294 | 0 | 0 | 3.1417 | 6.0158 | 14.2261 | 28.2649 | 44.1998 | 58.9878 | 59.354 | 58.7657 | 57.623 | 37.168 | 20.0051 | 20.2261 | 34.3879 | 53.4184 | 56.8057 | 51.9004 | 43.5426 | 45.439 | 38.7975 | 58.3338 | 57.5147 | 57.3156
295 | 32.9038 | 24.6992 | 23.9627 | 20.5234 | 14.2548 | 4.8621 | 0 | 0 | 0 | 0 | 0.17297 | 6.9619 | 13.4119 | 9.4711 | 14.2086 | 22.3063 | 3.5488 | 5.2058 | 13.7255 | 11.1205 | 7.947 | 10.3479 | 13.8966 | 8.5455
296 | 22.9298 | 18.8801 | 11.3202 | 14.5515 | 5.27 | 5.5266 | 6.7852 | 8.6798 | 5.938 | 8.3503 | 9.4759 | 11.6529 | 11.0739 | 10.1801 | 26.1708 | 30.2367 | 10.647 | 33.3146 | 14.919 | 39.7243 | 16.2 | 2.4639 | 0.30559 | 0.04048
297 | 19.2507 | 9.7339 | 5.9161 | 8.7805 | 7.8744 | 19.0278 | 19.8604 | 35.7099 | 14.2118 | 6.4203 | 5.9865 | 7.8812 | 2.9875 | 2.1005 | 4.1957 | 9.8818 | 23.4974 | 59.4 | 59.4 | 58.9427 | 56.7243 | 55.199 | 58.3447 | 59.2623
298 | 59.4 | 59.4 | 59.4 | 58.9553 | 59.4 | 57.9592 | 45.486 | 33.9859 | 13.1725 | 1.6779 | 1.0513 | 6.1493 | 4.5732 | 0.71865 | 0 | 0 | 0.31635 | 1.3889 | 1.2903 | 0.14587 | 1.9836 | 2.8171 | 0.24864 | 6.9028
299 | 19.0623 | 18.3653 | 14.7664 | 17.7248 | 18.3549 | 25.7962 | 29.9871 | 25.5125 | 14.1293 | 9.1287 | 5.1578 | 1.3481 | 0.61748 | 1.803 | 4.3519 | 7.9064 | 18.7426 | 28.8648 | 29.0497 | 21.0576 | 17.4195 | 1.509 | 0 | 5.3756
300 | 8.3143 | 12.0375 | 12.135 | 16.9949 | 21.1114 | 21.8262 | 17.61 | 12.8307 | 5.7889 | 0 | 0 | 2.3229 | 12.0642 | 25.1384 | 18.016 | 14.9134 | 20.8142 | 15.0532 | 34.6073 | 39.452 | 48.6418 | 50.7103 | 55.747 | 57.1566
301 | 26.0886 | 36.5879 | 33.0328 | 32.1349 | 33.0044 | 34.8597 | 25.7091 | 25.6648 | 20.6299 | 19.6593 | 43.1543 | 53.0483 | 48.91 | 32.4375 | 47.147 | 20.3311 | 13.0099 | 5.8581 | 0 | 5.1031 | 4.7738 | 57.8865 | 54.3737 | 57.9261
302 | 57.2982 | 51.5646 | 56.3416 | 57.5357 | 59.1387 | 52.4036 | 36.2092 | 27.6482 | 14.3277 | 14.4048 | 19.3315 | 8.0279 | 0.2534 | 1.7349 | 25.6304 | 29.5989 | 28.9562 | 59.4 | 59.4 | 59.3219 | 59.4 | 58.868 | 57.6895 | 55.5432
303 | 54.7043 | 43.4062 | 36.0132 | 37.477 | 34.2053 | 44.2844 | 55.8987 | 59.1234 | 58.8488 | 59.2205 | 59.4 | 59.3952 | 59.4 | 53.536 | 26.5844 | 13.3927 | 8.7025 | 23.908 | 51.5318 | 56.9093 | 54.5936 | 59.2306 | 57.006 | 35.8423
304 | 26.3929 | 16.3682 | 11.7128 | 18.077 | 26.0289 | 33.646 | 46.8055 | 54.1426 | 32.6419 | 32.426 | 31.6162 | 32.4573 | 52.2045 | 57.8195 | 59.4 | 58.0803 | 59.2471 | 59.2068 | 59.0903 | 59.4 | 59.2597 | 58.891 | 58.1944 | 57.827
305 | 59.3991 | 59.3424 | 57.4628 | 50.1476 | 55.6386 | 52.2132 | 33.3864 | 18.6038 | 12.5761 | 2.1181 | 5.4939 | 3.3833 | 0.69743 | 0 | 0 | 3.8597 | 16.211 | 19.6359 | 20.1612 | 4.638 | 6.1715 | 5.148 | 15.8319 | 9.8878
306 | 9.2364 | 15.1097 | 15.9739 | 19.7688 | 24.921 | 25.7857 | 21.1178 | 12.542 | 4.8246 | 0.1445 | 0 | 0 | 0 | 0 | 1.3864 | 8.7793 | 19.06 | 43.3753 | 59.4 | 59.3037 | 58.6352 | 59.3811 | 59.4 | 59.286
307 | 57.1341 | 53.899 | 36.8323 | 26.9466 | 16.9316 | 9.4945 | 6.7492 | 8.9033 | 11.4703 | 8.0896 | 2.6288 | 0 | 0 | 0 | 0.45205 | 2.4361 | 5.4071 | 9.4084 | 18.0484 | 32.1247 | 33.8446 | 36.4851 | 20.2087 | 15.3806
308 | 3.7906 | 3.1255 | 9.583 | 16.9162 | 19.7852 | 14.1589 | 14.0811 | 16.437 | 27.3445 | 13.4068 | 5.4058 | 8.6772 | 17.2852 | 22.1499 | 38.1114 | 57.2667 | 59.4 | 59.4 | 59.2591 | 59.0738 | 59.4 | 59.4 | 59.4 | 59.2776
309 | 59.0263 | 58.7222 | 59.3788 | 42.6446 | 22.0412 | 7.8561 | 3.0505 | 4.226 | 8.8678 | 9.0431 | 11.2759 | 12.3869 | 11.5603 | 7.8527 | 5.9619 | 4.27 | 2.9412 | 1.8123 | 0.7467 | 0.12453 | 21.4969 | 40.7845 | 44.1395 | 52.483
310 | 26.3815 | 22.1078 | 17.2839 | 12.5176 | 6.2 | 0.29269 | 0 | 0 | 0 | 2.0624 | 5.7044 | 8.5224 | 11.956 | 9.1056 | 9.282 | 18.491 | 25.1073 | 37.007 | 39.6378 | 36.7867 | 35.7052 | 20.1408 | 23.4944 | 35.9165
311 | 56.8584 | 59.4 | 59.4 | 59.4 | 58.6981 | 51.5063 | 45.9395 | 48.6329 | 40.6507 | 27.2915 | 24.5741 | 21.4784 | 15.735 | 3.0605 | 28.8475 | 42.2319 | 6.6381 | 59.3699 | 58.9029 | 57.3405 | 57.3555 | 58.117 | 59.3657 | 59.4
312 | 54.1819 | 57.5132 | 58.0621 | 54.2022 | 7.6053 | 9.5066 | 53.8173 | 54.6175 | 54.2896 | 27.934 | 7.6053 | 54.5666 | 58.754 | 59.4 | 59.2802 | 52.0969 | 51.3922 | 47.3703 | 59.4 | 51.4217 | 30.6652 | 4.4821 | 0.74706 | 0
313 | 0.50424 | 31.5599 | 55.7128 | 35.8642 | 32.9888 | 8.2297 | 1.2983 | 0 | 0 | 0 | 0.63775 | 1.9553 | 4.7829 | 7.8915 | 12.2024 | 21.6716 | 33.5153 | 50.1792 | 50.9804 | 38.5461 | 24.3594 | 16.5968 | 7.2603 | 0
314 | 0 | 0 | 0.43802 | 6.4031 | 13.1742 | 14.9863 | 16.3421 | 19.9649 | 22.1089 | 13.5513 | 7.6421 | 3.9044 | 1.2798 | 0.032039 | 0.17595 | 0.48492 | 0 | 0 | 1.0635 | 3.3444 | 6.9987 | 3.2434 | 2.3392 | 2.9421
315 | 4.428 | 8.1516 | 8.1457 | 12.7499 | 27.1847 | 32.9159 | 47.8168 | 45.0688 | 43.7615 | 32.7209 | 27.557 | 8.5718 | 4.6392 | 2.08 | 3.5588 | 11.2701 | 23.6971 | 39.4164 | 26.9319 | 36.5653 | 26.765 | 23.6337 | 13.484 | 8.5442
316 | 7.1707 | 2.5762 | 0.31242 | 0.15627 | 0.27117 | 0.22944 | 0.44694 | 0.76144 | 2.2603 | 0 | 0 | 0 | 0 | 0 | 2.4676 | 3.8041 | 10.2356 | 13.287 | 17.7214 | 21.5307 | 13.0921 | 12.922 | 24.9084 | 50.8897
317 | 44.9086 | 55.8699 | 58.7251 | 59.4 | 59.3954 | 59.174 | 59.4 | 59.3824 | 58.0621 | 51.2695 | 52.1969 | 39.4633 | 27.2871 | 24.5112 | 27.0826 | 57.2496 | 59.4 | 59.4 | 59.1691 | 59.4 | 59.2678 | 53.5447 | 41.3479 | 37.3649
318 | 33.7152 | 30.8992 | 29.0282 | 28.4832 | 23.3681 | 17.6111 | 27.2238 | 58.704 | 59.4 | 57.9979 | 43.2899 | 21.82 | 10.7602 | 3.2732 | 3.3174 | 9.5271 | 7.2785 | 14.457 | 25.644 | 53.9535 | 57.5417 | 42.6721 | 34.4944 | 58.7816
319 | 59.4 | 59.4 | 59.4 | 59.4 | 59.4 | 59.1614 | 50.5577 | 37.922 | 37.4187 | 48.1784 | 43.8683 | 23.5526 | 9.9251 | 3.1456 | 0.4048 | 0.27408 | 0 | 0 | 0 | 0 | 0 | 0 | 11.0814 | 25.9533
320 | 33.136 | 22.0737 | 6.6744 | 1.9411 | 0 | 0 | 0.82552 | 1.4056 | 0.84704 | 0.72869 | 3.654 | 5.9898 | 12.1334 | 15.5615 | 18.6147 | 20.8817 | 25.867 | 22.0662 | 14.5596 | 18.7454 | 14.2765 | 21.7538 | 22.5532 | 36.0725
321 | 41.7337 | 19.2268 | 6.8097 | 2.4114 | 0.4832 | 0.14498 | 1.1613 | 10.2787 | 11.7248 | 27.1355 | 44.11 | 58.4711 | 59.4 | 59.4 | 59.4 | 59.3787 | 58.9647 | 49.3985 | 38.9147 | 15.7478 | 2.9932 | 0 | 0 | 0
322 | 1.1826 | 7.4376 | 17.6654 | 24.3016 | 40.686 | 54.2686 | 59.3936 | 59.4 | 59.1838 | 53.7165 | 46.2369 | 27.8054 | 28.5442 | 35.532 | 50.9623 | 59.4 | 58.0873 | 58.554 | 59.278 | 59.0611 | 46.6582 | 25.7174 | 25.3242 | 18.1951
323 | 32.3198 | 42.9293 | 59.0443 | 37.8635 | 11.6712 | 17.124 | 39.3743 | 51.6339 | 55.7368 | 59.4 | 59.4 | 59.4 | 59.4 | 59.4 | 59.3515 | 52.7117 | 37.5605 | 25.2492 | 4.9367 | 6.6496 | 3.3084 | 5.3656 | 7.9807 | 10.9084
324 | 9.6464 | 14.3915 | 19.2965 | 33.4113 | 43.3529 | 37.8114 | 26.1754 | 25.2395 | 25.564 | 20.8422 | 14.3854 | 14.6629 | 15.5329 | 16.6619 | 14.5262 | 10.4327 | 23.0931 | 19.0689 | 3.8074 | 7.3482 | 10.8632 | 7.9595 | 10.3165 | 22.6514
325 | 38.4736 | 37.8638 | 36.1548 | 39.0819 | 43.007 | 36.1691 | 27.9269 | 19.1675 | 16.6823 | 13.5032 | 3.8824 | 2.4855 | 1.4318 | 0 | 0 | 0 | 0.29305 | 7.3439 | 17.8614 | 20.374 | 28.1936 | 37.3622 | 47.0935 | 33.5539
326 | 18.6676 | 30.0067 | 21.5546 | 27.5272 | 28.606 | 34.857 | 42.4215 | 53.6616 | 56.3412 | 38.2107 | 15.6797 | 4.972 | 2.1297 | 0 | 0 | 0 | 6.1909 | 11.7241 | 23.2589 | 32.0527 | 30.1006 | 41.2451 | 56.4358 | 57.1622
327 | 52.3128 | 49.6544 | 45.9158 | 49.7838 | 53.0277 | 54.2725 | 52.3901 | 55.2552 | 50.0794 | 44.8111 | 32.3281 | 39.1121 | 49.667 | 50.9134 | 48.5825 | 35.9365 | 23.1569 | 11.2529 | 4.9466 | 5.3882 | 7.9896 | 8.6808 | 9.9581 | 12.8056
328 | 13.8943 | 8.6906 | 12.5663 | 12.152 | 8.7804 | 4.6647 | 3.0879 | 2.5749 | 2.7353 | 3.6786 | 0.9085 | 0 | 1.3052 | 0.59465 | 1.4811 | 4.7164 | 2.8885 | 1.3554 | 0 | 0 | 11.9001 | 37.806 | 56.468 | 52.7983
329 | 50.3579 | 54.2458 | 54.6439 | 53.0183 | 47.7118 | 43.2288 | 43.424 | 33.596 | 13.2947 | 8.6522 | 5.9189 | 0.74189 | 0 | 0 | 0 | 1.7633 | 6.6975 | 19.4975 | 51.0474 | 55.4816 | 53.6324 | 17.2396 | 10.7802 | 25.79
330 | 35.099 | 53.9838 | 59.4 | 59.3802 | 56.8947 | 38.2188 | 36.1663 | 37.4712 | 19.9182 | 12.8197 | 25.3755 | 48.9077 | 57.9023 | 35.4224 | 7.6942 | 1.0849 | 7.1253 | 9.7174 | 6.0387 | 10.5171 | 15.2334 | 7.9525 | 5.2215 | 5.1467
331 | 15.2335 | 37.702 | 38.7305 | 27.3186 | 20.4758 | 16.4746 | 19.1282 | 22.1687 | 17.6635 | 13.6553 | 6.8668 | 2.6056 | 0.76495 | 1.0254 | 1.9869 | 1.8855 | 0 | 0 | 0.29418 | 7.0104 | 10.6826 | 16.4877 | 15.7772 | 25.7469
332 | 37.5812 | 37.7659 | 33.5679 | 31.5961 | 36.2033 | 38.3115 | 40.0146 | 34.4025 | 27.0137 | 7.6292 | 0 | 0.038696 | 35.9613 | 40.6855 | 28.8983 | 18.3054 | 10.3049 | 7.8969 | 11.6998 | 18.1808 | 17.9602 | 15.6273 | 16.3577 | 15.8468
333 | 11.9593 | 5.5319 | 1.2121 | 0 | 0 | 0.081554 | 3.1159 | 3.3912 | 1.889 | 0.68399 | 0 | 0.033109 | 0.51328 | 1.2636 | 3.1981 | 1.5676 | 0.89679 | 8.1467 | 26.5113 | 9.7697 | 22.924 | 50.8364 | 57.4408 | 58.8091
334 | 58.3114 | 58.0075 | 58.3423 | 53.8861 | 47.1849 | 55.502 | 52.2767 | 58.12 | 48.5609 | 7.0102 | 0 | 1.8036 | 13.9723 | 47.7716 | 58.9591 | 6.6681 | 1.5485 | 39.9859 | 38.3874 | 20.5643 | 6.5476 | 0.60398 | 1.1245 | 0
335 | 0 | 6.0514 | 23.6788 | 22.1402 | 3.6496 | 3.1598 | 3.85 | 3.2238 | 1.1362 | 3.7778 | 4.2052 | 2.2949 | 0.72245 | 0 | 0.18451 | 5.0242 | 10.3033 | 22.9047 | 25.5978 | 29.7325 | 47.1207 | 44.6745 | 34.8784 | 28.6431
336 | 9.7219 | 1.6545 | 0 | 0 | 2.3465 | 6.7167 | 4.8738 | 1.7896 | 0.39124 | 0 | 0 | 0.44438 | 0.23592 | 1.9381 | 1.7869 | 0.66515 | 0.48094 | 4.4031 | 3.9436 | 4.2533 | 2.2754 | 11.3014 | 21.4456 | 30.5931
337 | 46.4393 | 45.294 | 21.1743 | 10.2948 | 6.2215 | 3.4515 | 3.1676 | 14.8071 | 45.5687 | 49.2297 | 26.9787 | 22.7474 | 32.2431 | 42.9432 | 37.6455 | 16.3017 | 4.9613 | 0.28776 | 0 | 0.3047 | 1.2282 | 1.654 | 4.2388 | 1.9746
338 | 0.94482 | 0.7089 | 2.7164 | 4.5929 | 8.3894 | 7.6571 | 8.078 | 13.1547 | 18.3885 | 13.5126 | 28.1064 | 26.0161 | 22.1162 | 13.9875 | 7.8269 | 6.2182 | 7.9536 | 13.6748 | 21.4844 | 23.8549 | 21.7197 | 10.8573 | 0.61213 | 0
339 | 7.8069 | 21.7705 | 36.5817 | 44.665 | 57.088 | 58.594 | 59.4 | 59.4 | 59.4 | 58.6441 | 56.4753 | 46.2484 | 20.3473 | 2.9703 | 0.083693 | 46.0138 | 59.4 | 57.689 | 47.726 | 42.6127 | 59.1772 | 59.006 | 52.8609 | 28.0405
340 | 10.3538 | 2.135 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4412 | 15.7346 | 6.2517 | 7.147 | 6.4042 | 3.1562 | 7.9367 | 21.3993 | 41.2083 | 49.6118 | 59.3111 | 33.168 | 17.4205 | 9.6069 | 14.9738 | 34.0007
341 | 51.963 | 58.3784 | 59.2807 | 59.4 | 59.3222 | 59.4 | 59.4 | 59.2153 | 48.8288 | 7.8583 | 0.50359 | 0 | 0.36194 | 7.9459 | 13.4886 | 28.0106 | 27.0801 | 17.243 | 13.2997 | 14.412 | 18.3403 | 13.4599 | 11.2916 | 6.4084
342 | 7.4209 | 12.1798 | 9.7469 | 6.2388 | 7.1117 | 5.5071 | 5.1589 | 5.2498 | 5.7967 | 7.5171 | 9.7952 | 11.4006 | 13.2254 | 19.6737 | 19.1537 | 18.4805 | 11.5257 | 20.4589 | 18.2451 | 20.692 | 26.7832 | 33.6338 | 7.4849 | 2.2549
343 | 1.8523 | 0 | 0 | 2.9307 | 6.6716 | 10.4904 | 15.8245 | 24.5065 | 21.809 | 16.6061 | 19.9715 | 17.0808 | 19.3696 | 19.6299 | 11.8756 | 0.82629 | 6.1102 | 9.6143 | 13.7875 | 17.5885 | 22.695 | 22.3665 | 38.2148 | 38.5564
344 | 31.5812 | 18.5199 | 11.6042 | 8.57 | 6.3273 | 5.4262 | 4.6785 | 5.5876 | 5.64 | 1.8994 | 1.7911 | 6.2131 | 5.6957 | 11.4288 | 14.6005 | 8.8724 | 2.5505 | 0.98488 | 0 | 2.5788 | 6.3364 | 9.718 | 4.9317 | 12.5689
345 | 39.764 | 26.2783 | 25.8501 | 45.0598 | 43.754 | 33.3808 | 16.3545 | 41.5973 | 24.2545 | 19.8613 | 14.7503 | 12.4124 | 9.7133 | 6.6369 | 3.1425 | 2.858 | 4.1372 | 4.731 | 6.9924 | 8.575 | 8.5939 | 7.7441 | 6.9634 | 6.1892
346 | 5.7022 | 5.5877 | 6.0848 | 4.5046 | 4.7329 | 3.2854 | 2.6162 | 0.16251 | 0 | 0 | 0 | 0.25405 | 6.7035 | 36.1873 | 58.5524 | 58.3761 | 59.3592 | 59.0433 | 59.2767 | 59.4 | 59.4 | 59.156 | 59.124 | 43.4491
347 | 18.9455 | 4.0622 | 2.621 | 3.5538 | 1.1494 | 0 | 6.3998 | 9.1067 | 16.9291 | 9.5704 | 17.2425 | 35.9337 | 52.269 | 46.5073 | 37.7303 | 33.1828 | 17.6204 | 4.2564 | 11.4606 | 24.4607 | 30.3924 | 24.3585 | 22.7735 | 21.4674
348 | 19.1864 | 18.6211 | 16.1978 | 14.1495 | 18.7566 | 20.8912 | 23.2805 | 24.0895 | 15.0479 | 18.9249 | 28.7979 | 38.6079 | 33.1874 | 24.3876 | 19.5215 | 17.3273 | 14.3623 | 16.6523 | 16.4051 | 28.622 | 41.0328 | 59.4 | 58.9758 | 58.6594
349 | 59.4 | 58.416 | 57.019 | 52.9554 | 55.068 | 58.1514 | 59.3577 | 59.4 | 57.7595 | 57.5989 | 58.8627 | 57.2445 | 55.8957 | 57.5204 | 57.9098 | 56.6532 | 51.3248 | 57.0224 | 50.2775 | 40.1793 | 58.0994 | 59.2155 | 59.4 | 59.1933
350 | 59.3399 | 55.3586 | 59.339 | 59.2326 | 59.3893 | 56.3884 | 38.1769 | 11.934 | 5.689 | 0.35665 | 3.5282 | 16.5633 | 26.375 | 24.7087 | 19.9498 | 20.6274 | 44.8324 | 59.4 | 59.3692 | 59.4 | 59.4 | 59.3172 | 51.9923 | 47.6615
351 | 59.2951 | 59.4 | 59.4 | 59.338 | 59.178 | 59.2222 | 57.4174 | 51.6046 | 38.0265 | 34.403 | 57.8865 | 57.0344 | 11.4079 | 9.5066 | 58.0952 | 59.3348 | 59.3576 | 54.3244 | 53.047 | 59.4 | 58.274 | 58.8192 | 59.2987 | 59.4
352 | 59.4 | 59.3491 | 59.1211 | 59.4 | 59.2194 | 54.5624 | 45.0346 | 36.7093 | 25.6803 | 55.2169 | 58.9916 | 59.0635 | 59.3931 | 59.4 | 59.4 | 59.0595 | 56.7818 | 49.1047 | 32.7111 | 37.5867 | 22.0397 | 17.3834 | 8.5455 | 5.3913
353 | 19.2795 | 27.5693 | 25.9643 | 48.0139 | 58.8231 | 59.2395 | 57.4234 | 54.8536 | 51.9911 | 53.777 | 55.0814 | 56.4385 | 57.836 | 59.1253 | 59.3723 | 59.4 | 59.4 | 56.4891 | 51.6197 | 56.2615 | 58.9443 | 59.3749 | 58.7324 | 50.3212
354 | 44.7806 | 46.0686 | 40.4462 | 37.0271 | 51.064 | 58.3188 | 57.8863 | 48.6612 | 23.2402 | 12.5654 | 34.6104 | 59.4 | 49.5457 | 57.7462 | 49.984 | 59.3938 | 31.9538 | 17.0436 | 7.2543 | 2.793 | 2.0816 | 7.408 | 16.4829 | 41.4642
355 | 46.3278 | 35.0071 | 22.086 | 5.2899 | 2.6133 | 1.4937 | 0.40331 | 0 | 0 | 0 | 0 | 0 | 0.89721 | 8.298 | 14.9606 | 13.7559 | 22.6245 | 31.0149 | 32.3502 | 23.5657 | 35.0057 | 44.3323 | 57.8844 | 59.4
356 | 18.6293 | 17.2276 | 9.8163 | 4.1338 | 0.34232 | 0 | 0 | 0.24924 | 0.40206 | 1.8347 | 8.1237 | 13.8582 | 14.4502 | 20.9877 | 24.0578 | 29.6534 | 44.9756 | 20.3296 | 13.5837 | 6.932 | 8.4009 | 8.1432 | 7.1261 | 5.6171
357 | 5.7279 | 6.0684 | 5.7829 | 5.7937 | 6.911 | 5.3767 | 3.9828 | 3.1267 | 2.4943 | 2.8627 | 5.5034 | 11.7635 | 17.0549 | 18.0647 | 14.0553 | 11.7238 | 10.1021 | 13.8109 | 11.1319 | 15.326 | 10.7134 | 13.5424 | 13.1653 | 8.5736
358 | 9.053 | 13.8612 | 14.2168 | 15.0743 | 18.959 | 17.4711 | 13.3252 | 19.2962 | 15.1361 | 15.7857 | 18.007 | 25.8011 | 34.1459 | 35.5411 | 26.8362 | 19.657 | 17.4361 | 14.762 | 11.1743 | 12.5128 | 10.0336 | 5.6089 | 3.7129 | 4.2894
359 | 4.683 | 4.6957 | 2.526 | 0.14415 | 0 | 0 | 0 | 0 | 0 | 0.55185 | 2.3552 | 5.5534 | 7.9506 | 11.8989 | 13.8354 | 11.7198 | 7.8801 | 6.9044 | 4.3058 | 2.3745 | 0.90042 | 1.5111 | 4.7942 | 10.8843
360 | 17.0917 | 35.3321 | 49.0613 | 10.4142 | 47.5383 | 29.0657 | 38.1412 | 35.2313 | 26.8339 | 21.2593 | 10.0966 | 7.6609 | 4.647 | 8.113 | 13.9713 | 23.767 | 58.8036 | 59.4 | 59.3306 | 59.299 | 59.4 | 59.4 | 59.4 | 59.4
361 | 59.4 | 59.3111 | 59.3761 | 58.6465 | 58.8369 | 56.4406 | 52.8807 | 53.6029 | 52.8008 | 23.7877 | 5.7292 | 9.4907 | 9.3505 | 8.7299 | 29.3193 | 25.2769 | 27.354 | 24.4029 | 16.5257 | 15.3408 | 4.018 | 3.0439 | 8.4243 | 8.7495
362 | 8.6542 | 8.2809 | 10.6205 | 8.7623 | 3.8689 | 1.9296 | 1.9208 | 56.3816 | 38.4464 | 24.1424 | 14.7509 | 8.459 | 1.5066 | 0 | 0.081256 | 3.918 | 7.3596 | 10.414 | 9.315 | 10.33 | 14.9398 | 19.5162 | 21.3338 | 20.5477
363 | 12.8943 | 5.2682 | 0.93258 | 0.048385 | 0.39511 | 1.1293 | 0.5805 | 0 | 0 | 0 | 0 | 3.296 | 6.6196 | 7.7178 | 6.8291 | 6.639 | 12.6009 | 23.7993 | 33.5707 | 38.2844 | 49.8911 | 50.974 | 46.7899 | 48.1223
364 | 53.6988 | 52.611 | 48.0176 | 50.1763 | 56.3475 | 55.7026 | 57.2553 | 58.7058 | 58.0502 | 50.9589 | 45.5491 | 45.5065 | 35.3799 | 30.5188 | 31.8546 | 50.003 | 59.3345 | 59.3044 | 58.302 | 57.2233 | 58.2184 | 58.0218 | 56.0386 | 57.642
365 | 54.8386 | 53.9533 | 59.0095 | 59.4 | 59.4 | 59.3084 | 32.8378 | 19.0695 | 16.1505 | 1.0046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36016 | 4.9934 | 7.4947 | 12.8461 | 15.4584 | 16.9488
TMY - Energy Profile
version 1-1c
CLIENT: BLACK HILLS CORP.
PROJECT: BUSCH RANCH II
TURBINE: VESTAS V120-2.2MW
HUB HEIGHT: 80M
ALL DATA PRESENTED IN THIS PRELIMINARY REPORT ARE DRAFT AND ARE SUBJECT TO CHANGE DURING THE FINAL QUALITY CONTROL PROCESS.

## 12x24
Date are in local time (UTC -7)
Values represent the average value for each hour of the each month based on the 37-year timeseries
MWh | HOUR
Month | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Total
1 | 27.3 | 27.1 | 27.1 | 26.8 | 26.5 | 27.3 | 26.7 | 25.8 | 25.8 | 24.8 | 21.7 | 20 | 19.6 | 19.4 | 20.1 | 20.1 | 20.5 | 22.7 | 25.7 | 26.4 | 26.8 | 27.2 | 26.9 | 27 | 18268.3
2 | 25 | 25.5 | 26 | 25.3 | 24.8 | 25.7 | 25.1 | 24.4 | 24.6 | 23.3 | 21.3 | 19.9 | 19.1 | 19.2 | 19.8 | 20.2 | 21.2 | 23.2 | 24.5 | 25.4 | 26.5 | 26 | 25.3 | 25.8 | 17580.1
3 | 26.6 | 25.8 | 25.8 | 24.9 | 25 | 25.6 | 24.7 | 23.7 | 22.8 | 20.9 | 20.7 | 20.7 | 20.7 | 21.4 | 22.7 | 23.6 | 25.4 | 25.8 | 26.8 | 27.3 | 27.9 | 27.6 | 27.2 | 26.7 | 17118.7
4 | 28.8 | 27.4 | 27.1 | 25.6 | 24.8 | 24.5 | 24.7 | 23.8 | 20.8 | 20.2 | 19.8 | 20.1 | 21.1 | 22.2 | 23.8 | 25.3 | 25.1 | 26.6 | 27.7 | 29.1 | 29.5 | 30 | 29.5 | 28.8 | 18795.3
5 | 27.2 | 24.9 | 24.4 | 24.1 | 23.4 | 21.9 | 20.9 | 18.3 | 15.6 | 15.1 | 15.7 | 17.1 | 19.3 | 20.2 | 22.8 | 25.1 | 26.5 | 28.2 | 29.1 | 29.6 | 30.6 | 29.6 | 29.1 | 29.1 | 17034
6 | 29.6 | 27.5 | 26.1 | 24.4 | 23.4 | 21.9 | 19 | 16.5 | 14.6 | 14.2 | 14.3 | 15.4 | 17 | 16.9 | 18.8 | 23.8 | 25.7 | 28.9 | 30.2 | 30.1 | 31.7 | 31.1 | 30.4 | 30.5 | 17422
7 | 27.5 | 25.6 | 24.6 | 22.5 | 19.8 | 18.4 | 16.6 | 13.3 | 10.8 | 10.8 | 10.2 | 9.4 | 9.8 | 9.8 | 11.7 | 14.5 | 18.1 | 22.5 | 23.8 | 24.3 | 27.6 | 28.1 | 26.8 | 27.4 | 13617
8 | 26.7 | 25.1 | 23.7 | 23 | 22.2 | 20.4 | 19.2 | 16.4 | 12.2 | 11.1 | 10 | 9.1 | 8.9 | 9.7 | 12.3 | 14 | 16.4 | 20.7 | 23.4 | 24.6 | 26 | 26.2 | 26.6 | 27.3 | 14111.2
9 | 27.5 | 24.6 | 23.6 | 23 | 22.7 | 22.1 | 21.2 | 19.6 | 15.8 | 14.3 | 14 | 13.8 | 13.7 | 14.7 | 15.9 | 16.4 | 18.4 | 21.2 | 24.9 | 27.8 | 27.9 | 28.8 | 28.1 | 27.8 | 15741.8
10 | 24.6 | 24.3 | 23.9 | 24.1 | 24.4 | 25 | 24.1 | 23.5 | 21.9 | 19.4 | 17.7 | 16.7 | 16 | 16.9 | 17.9 | 19.1 | 21.3 | 23.4 | 25.2 | 26.4 | 26.9 | 26.3 | 25.2 | 24.7 | 16167
11 | 26.5 | 26.9 | 26.7 | 26.6 | 26.9 | 26.9 | 26.2 | 25.7 | 25.1 | 23 | 20.9 | 19.8 | 19.2 | 19.7 | 19.9 | 20.4 | 22.3 | 24.5 | 26.7 | 27.9 | 28 | 27.3 | 25.9 | 25.9 | 18255.9
12 | 26.3 | 27.3 | 28 | 27.6 | 27 | 26.8 | 25.9 | 25.2 | 25.3 | 24.6 | 22.6 | 21.1 | 20.9 | 20.8 | 21.1 | 21.1 | 21.8 | 23.3 | 25.8 | 26.7 | 26.7 | 26.8 | 26.4 | 25.9 | 17850
[25 empty] | 201961.3 | MWh
12x24 - Energy Profile
version 1-1
CLIENT: BLACK HILLS CORP.
PROJECT: BUSCH RANCH II
TURBINE: VESTAS V120-2.2MW
HUB HEIGHT: 80M
ALL DATA PRESENTED IN THIS PRELIMINARY REPORT ARE DRAFT AND ARE SUBJECT TO CHANGE DURING THE FINAL QUALITY CONTROL PROCESS.